## 681-9-2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
S&C "K" Speed (TCC 681-9-2) | [9 empty] | S&C "K" Speed (TCC 681-9-2) | [9 empty] | S&C "K" Speed (TCC 681-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
25K |  | 30K |  | 40K |  | 50K |  | 65K |  | 80K |  | 100K |  | 125K |  | 150K |  | 175K |  | 200K
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.0415 | 25000 | 0.042 | 25000 | 0.0434
4713 | 0.041 | 4864 | 0.041 | 5322 | 0.041 | 5775 | 0.041 | 11576 | 0.041 | 14883 | 0.041 | 17640 | 0.041 | 15000 | 0.0412 | 20000 | 0.0418 | 18000 | 0.0428 | 22000 | 0.044
2100 | 0.045 | 2251 | 0.045 | 2709 | 0.045 | 3162 | 0.045 | 7827 | 0.042 | 10143 | 0.042 | 10143 | 0.043 | 12678 | 0.0423 | 15986 | 0.0429 | 15000 | 0.044 | 18000 | 0.0455
1775 | 0.047 | 1926 | 0.047 | 2384 | 0.047 | 2837 | 0.047 | 6504 | 0.043 | 8213 | 0.043 | 8820 | 0.044 | 11025 | 0.0432 | 13781 | 0.044 | 12678 | 0.046 | 13196.925 | 0.05
1560 | 0.049 | 1711 | 0.049 | 2169 | 0.049 | 2622 | 0.049 | 5512 | 0.044 | 7056 | 0.044 | 7827 | 0.045 | 9922 | 0.0442 | 12127 | 0.045 | 10000 | 0.051 | 9531.1125 | 0.06
1461.926 | 0.05 | 1612.4504 | 0.05 | 2070.4178 | 0.05 | 2523.7658 | 0.05 | 4961 | 0.045 | 6229 | 0.045 | 6835 | 0.046 | 8930 | 0.0457 | 11025 | 0.046 | 7855.3125 | 0.06 | 7907.6813 | 0.07
1428.6856 | 0.05045 | 1583.6861 | 0.050377 | 2039.603 | 0.050325 | 2493.6676 | 0.050284 | 4520 | 0.046 | 5733 | 0.046 | 6394 | 0.047 | 8268 | 0.0468 | 10032 | 0.047 | 6546.0938 | 0.07 | 6210.9338 | 0.09
1348.1701 | 0.051747 | 1539.9499 | 0.050964 | 1983.2762 | 0.05092 | 2434.5295 | 0.050811 | 4189 | 0.047 | 5236 | 0.047 | 6063 | 0.048 | 7717 | 0.048 | 9371 | 0.048 | 5184.5063 | 0.09 | 4503.7125 | 0.14
1269.661 | 0.053271 | 1481.0544 | 0.051829 | 1901.7133 | 0.051829 | 2357.8616 | 0.051514 | 3969 | 0.048 | 4851 | 0.048 | 5622 | 0.049 | 7386 | 0.049 | 8820 | 0.0492 | 3739.1288 | 0.14 | 3278.2838 | 0.24
1161.5499 | 0.055841 | 1408.8186 | 0.0531 | 1818.0335 | 0.052956 | 2272.2084 | 0.052386 | 3748 | 0.049 | 4575 | 0.049 | 5434.421 | 0.05 | 7122.15 | 0.05 | 8483.7375 | 0.05 | 2733.6488 | 0.24 | 2765.07 | 0.34
1080.859 | 0.058276 | 1320.1556 | 0.054933 | 1719.018 | 0.054463 | 2187.4813 | 0.053378 | 3454.7609 | 0.05 | 4374.3341 | 0.05 | 5353.5195 | 0.050377 | 5132.1375 | 0.06 | 6179.5125 | 0.06 | 2272.8038 | 0.34 | 2251.8563 | 0.54
989.808 | 0.061641 | 1235.8364 | 0.057023 | 1602.8035 | 0.056686 | 2087.0545 | 0.054652 | 3406.736 | 0.050336 | 4317.831 | 0.050325 | 5216.1149 | 0.050931 | 4294.2375 | 0.07 | 5132.1375 | 0.07 | 1853.8537 | 0.54 | 1738.6425 | 1.04
914.6219 | 0.06532 | 1148.8381 | 0.05968 | 1431.5411 | 0.060792 | 1963.5525 | 0.05657 | 3286.2658 | 0.051041 | 4190.2166 | 0.050942 | 5041.7546 | 0.051688 | 3351.6 | 0.09 | 4053.3412 | 0.09 | 1434.9037 | 1.04 | 1372.0612 | 2.04
847.6869 | 0.069417 | 1061.5774 | 0.063048 | 1307.0248 | 0.064968 | 1858.4732 | 0.058441 | 3170.0734 | 0.051889 | 3906.9403 | 0.052599 | 4800.6599 | 0.052879 | 2419.4363 | 0.14 | 2943.1238 | 0.14 | 1141.6388 | 2.04 | 1214.955 | 3.04
781.7309 | 0.074625 | 990.798 | 0.066432 | 1201.714 | 0.069506 | 1738.0251 | 0.061064 | 3045.7665 | 0.052827 | 3592.1545 | 0.054903 | 4566.5329 | 0.054248 | 1780.5375 | 0.24 | 2147.1188 | 0.24 | 995.0063 | 3.04 | 1047.375 | 5.04
710.1754 | 0.081955 | 907.3343 | 0.071519 | 1113.7676 | 0.074384 | 1649.9574 | 0.063443 | 2932.198 | 0.053868 | 3335.9335 | 0.057194 | 4177.6702 | 0.057023 | 1487.2725 | 0.34 | 1780.5375 | 0.34 | 858.8475 | 5.04 | 879.795 | 10.04
657.5442 | 0.088744 | 832.565 | 0.077472 | 1021.9943 | 0.080796 | 1536.874 | 0.066939 | 2717.6074 | 0.056112 | 3073.307 | 0.060299 | 3899.1346 | 0.059503 | 1204.4813 | 0.54 | 1455.8512 | 0.54 | 714.3098 | 10.04 | 752.0153 | 20.04
607.5966 | 0.096974 | 755.5995 | 0.085403 | 934.9674 | 0.088696 | 1464.8477 | 0.069654 | 2531.351 | 0.058571 | 2803.1724 | 0.064376 | 3595.7486 | 0.06291 | 942.6375 | 1.04 | 1131.165 | 1.04 | 612.7144 | 20.04 | 689.1728 | 30.04
542.1334 | 0.11149 | 688.4969 | 0.094794 | 858.7791 | 0.097661 | 1394.8058 | 0.072805 | 2343.7496 | 0.061641 | 2608.4378 | 0.068039 | 3345.9552 | 0.066406 | 743.6363 | 2.04 | 890.2688 | 2.04 | 570.8194 | 30.04 | 628.425 | 50.04
495.4723 | 0.12585 | 643.236 | 0.10265 | 780.9504 | 0.10959 | 1325.4476 | 0.076255 | 2112.2467 | 0.066485 | 2449.1817 | 0.071868 | 3024.5213 | 0.072414 | 656.7041 | 3.04 | 790.7681 | 3.04 | 532.0665 | 50.04 | 584.4352 | 100.04
455.0977 | 0.14115 | 601.5516 | 0.11156 | 714.4487 | 0.1229 | 1243.2782 | 0.081165 | 1932.3848 | 0.071677 | 2297.3454 | 0.076219 | 2766.9663 | 0.07869 | 565.5825 | 5.04 | 680.7938 | 5.04 | 494.361 | 100.04 | 555.1087 | 200.04
422.2134 | 0.15763 | 549.2269 | 0.12593 | 643.8798 | 0.14206 | 1183.8314 | 0.085403 | 1734.5632 | 0.079197 | 2142.0252 | 0.081454 | 2476.2701 | 0.088019 | 471.3188 | 10.04 | 568.7246 | 10.04 | 466.0819 | 200.04 | 544.635 | 300.04
391.7061 | 0.17654 | 514.1487 | 0.13786 | 584.9413 | 0.16367 | 1120.4707 | 0.090734 | 1563.2237 | 0.088308 | 1969.4509 | 0.089136 | 2279.0329 | 0.096917 | 403.2394 | 20.04 | 492.2663 | 20.04 | 455.6081 | 300.04 | 528.9244 | 600.04
355.4956 | 0.20511 | 474.6185 | 0.15496 | 535.1314 | 0.18761 | 1052.0661 | 0.097777 | 1431.5411 | 0.097546 | 1799.9415 | 0.098533 | 2051.8738 | 0.10994 | 374.9603 | 30.04 | 450.3712 | 30.04 | 443.0396 | 600.04
334.4577 | 0.2269 | 438.128 | 0.17504 | 486.6336 | 0.21797 | 993.7759 | 0.10469 | 1312.2617 | 0.10876 | 1674.896 | 0.1076 | 1884.6686 | 0.12265 | 344.5864 | 50.04 | 416.8553 | 50.04
311.5345 | 0.25477 | 405.6583 | 0.19721 | 443.4178 | 0.25413 | 904.6167 | 0.11791 | 1199.3215 | 0.12215 | 1569.4969 | 0.11691 | 1724.1777 | 0.13865 | 317.3546 | 100.04 | 384.3866 | 100.04
287.0083 | 0.29179 | 375.5953 | 0.22339 | 390.9233 | 0.31578 | 842.6154 | 0.12944 | 1096.0967 | 0.13865 | 1428.6856 | 0.13263 | 1582.0985 | 0.15717 | 305.8335 | 200.04 | 368.676 | 200.04
262.5681 | 0.34054 | 351.9577 | 0.24926 | 363.7666 | 0.35977 | 790.3778 | 0.14155 | 954.8091 | 0.16936 | 1318.8436 | 0.14848 | 1428.6856 | 0.18382 | 303.7387 | 300.04 | 366.5813 | 300.04
242.1388 | 0.39304 | 324.5738 | 0.28557 | 338.1577 | 0.40892 | 727.4251 | 0.16013 | 870.0158 | 0.19612 | 1215.0101 | 0.1668 | 1304.4119 | 0.21271 | 302.6914 | 600.04 | 363.4391 | 600.04
213.0471 | 0.49241 | 303.8435 | 0.32079 | 321.3435 | 0.45018 | 668.8173 | 0.18197 | 793.5453 | 0.22784 | 1100.4901 | 0.19394 | 1201.714 | 0.2443
192.7721 | 0.59203 | 274.9282 | 0.38295 | 306.2833 | 0.49196 | 579.1212 | 0.22878 | 731.0711 | 0.26132 | 979.9593 | 0.23395 | 1131.7383 | 0.27058
176.0042 | 0.69892 | 254.2993 | 0.44165 | 294.8636 | 0.53009 | 505.4819 | 0.28804 | 682.3284 | 0.29356 | 888.4794 | 0.27571 | 1067.9664 | 0.30076
161.9859 | 0.81402 | 231.7157 | 0.5228 | 278.8046 | 0.58872 | 458.2938 | 0.34145 | 643.236 | 0.32589 | 797.5231 | 0.33108 | 1007.7864 | 0.33489
151.1858 | 0.92767 | 211.9843 | 0.61398 | 267.8722 | 0.6374 | 410.5556 | 0.41638 | 598.5506 | 0.37016 | 729.6113 | 0.38571 | 954.8091 | 0.37182
141.2468 | 1.0652 | 189.1449 | 0.76169 | 258.4006 | 0.68522 | 382.799 | 0.47424 | 563.1305 | 0.41077 | 687.809 | 0.42939 | 883.1642 | 0.43056
131.698 | 1.2216 | 173.905 | 0.90316 | 247.5245 | 0.74669 | 362.3146 | 0.5228 | 532.4623 | 0.45347 | 651.6525 | 0.46949 | 834.232 | 0.4808
123.4094 | 1.3951 | 164.2703 | 1.0132 | 235.2173 | 0.82808 | 344.6437 | 0.57357 | 510.5622 | 0.49106 | 618.0141 | 0.51847 | 786.4364 | 0.5425
117.1561 | 1.5587 | 154.2398 | 1.1572 | 221.963 | 0.93748 | 331.1304 | 0.62091 | 491.0326 | 0.53058 | 589.0503 | 0.56826 | 742.1203 | 0.61055
110.2239 | 1.7904 | 145.6943 | 1.3085 | 208.8278 | 1.0693 | 314.9809 | 0.68522 | 471.7796 | 0.57091 | 553.0846 | 0.6416 | 703.8117 | 0.68072
104.9531 | 1.9939 | 137.3472 | 1.4948 | 199.0409 | 1.1878 | 298.7213 | 0.75953 | 441.6472 | 0.64947 | 522.4406 | 0.71898 | 671.4986 | 0.75166
99.2373 | 2.2741 | 131.0409 | 1.6623 | 190.8549 | 1.3022 | 284.7217 | 0.836 | 418.8497 | 0.72512 | 491.5243 | 0.81479 | 627.9818 | 0.86848
93.5516 | 2.6124 | 124.7743 | 1.8655 | 183.5541 | 1.4335 | 269.4841 | 0.93569 | 390.5331 | 0.83919 | 462.437 | 0.92501 | 599.1492 | 0.96389
90.0634 | 2.8716 | 119.0457 | 2.1023 | 176.7098 | 1.5663 | 257.3687 | 1.0289 | 368.5261 | 0.94923 | 440.3242 | 1.0259 | 563.1305 | 1.1123
85.329 | 3.2939 | 113.3535 | 2.3863 | 171.3164 | 1.6967 | 245.3074 | 1.1373 | 348.4562 | 1.0693 | 425.1791 | 1.1113 | 531.9298 | 1.2698
80.9243 | 3.8091 | 108.3659 | 2.6749 | 165.5889 | 1.8473 | 233.343 | 1.2686 | 328.1635 | 1.218 | 408.9172 | 1.2192 | 505.4819 | 1.4349
76.5171 | 4.4587 | 103.9089 | 3.0108 | 160.8559 | 1.9822 | 224.1934 | 1.3978 | 310.9127 | 1.3776 | 396.0389 | 1.306 | 487.1209 | 1.5678
73.8115 | 4.9824 | 100.0343 | 3.3662 | 155.6344 | 2.1737 | 213.2599 | 1.5693 | 297.2318 | 1.5256 | 383.1827 | 1.4087 | 473.6704 | 1.6868
71.2015 | 5.5792 | 96.4007 | 3.7679 | 150.7327 | 2.3699 | 205.1025 | 1.7251 | 283.0184 | 1.7285 | 368.1578 | 1.5541 | 457.3787 | 1.8564
68.6839 | 6.3041 | 93.4582 | 4.2014 | 145.1122 | 2.6305 | 197.2582 | 1.9005 | 271.3782 | 1.9154 | 355.4956 | 1.7 | 440.7652 | 2.0474
66.5208 | 7.1028 | 90.7868 | 4.6899 | 139.9811 | 2.9404 | 190.2827 | 2.09 | 263.8845 | 2.0655 | 342.9249 | 1.86 | 422.2134 | 2.3033
64.684 | 7.9636 | 88.3684 | 5.2618 | 134.6274 | 3.3134 | 182.0922 | 2.356 | 255.3181 | 2.2585 | 331.4611 | 2.0314 | 408.0992 | 2.5364
63.024 | 8.9204 | 85.671 | 6.0106 | 129.0895 | 3.7828 | 173.905 | 2.6775 | 247.5245 | 2.4821 | 319.1021 | 2.2541 | 394.8527 | 2.7962
61.1001 | 10.2446 | 83.5557 | 6.8191 | 125.5251 | 4.2014 | 166.5855 | 3.0198 | 240.4497 | 2.7014 | 305.6714 | 2.5389 | 380.8906 | 3.1044
59.7108 | 11.6846 | 81.0053 | 8.1479 | 122.6719 | 4.5933 | 160.535 | 3.3963 | 232.1799 | 2.9842 | 296.6375 | 2.7934 | 369.633 | 3.4131
58.8219 | 13.1692 | 78.8474 | 9.6696 | 120.0027 | 5.1227 | 155.1681 | 3.7903 | 225.0919 | 3.2841 | 285.0062 | 3.1507 | 360.5076 | 3.7308
57.7149 | 15.2635 | 76.747 | 11.7079 | 117.5089 | 5.7536 | 150.8837 | 4.1353 | 216.9158 | 3.6505 | 278.2478 | 3.4504 | 350.9037 | 4.1149
56.6853 | 18.1026 | 74.8521 | 14.1918 | 114.6071 | 6.5533 | 147.896 | 4.4631 | 210.0847 | 4.0582 | 269.2151 | 3.8699 | 344.2997 | 4.4499
55.7855 | 22.0797 | 73.1501 | 17.7449 | 112.9004 | 7.3252 | 145.1122 | 4.8028 | 205.5137 | 4.4104 | 264.6772 | 4.2222 | 337.1445 | 4.87
55.1201 | 26.5321 | 72.2054 | 19.9823 | 110.3338 | 8.5466 | 142.6668 | 5.2047 | 200.4389 | 4.8315 | 258.4006 | 4.676 | 330.1381 | 5.346
54.6809 | 32.2039 | 71.5584 | 22.5474 | 108.2577 | 9.8543 | 140.2623 | 5.6573 | 196.0774 | 5.2775 | 253.5375 | 5.1431 | 322.9542 | 5.9335
54.5171 | 39.7597 | 70.6342 | 26.5056 | 106.114 | 11.4198 | 137.8974 | 6.2109 | 191.6189 | 5.8748 | 249.0151 | 5.7308 | 317.5112 | 6.4885
54.5717 | 49.0413 | 70.0014 | 30.4523 | 104.2211 | 13.4077 | 135.4377 | 6.9353 | 187.8252 | 6.4563 | 243.8399 | 6.4692 | 311.8465 | 7.1453
54.6262 | 65.07 | 69.3742 | 35.3387 | 102.2595 | 16.2697 | 132.8887 | 7.7525 | 183.9224 | 7.2024 | 237.8192 | 7.4279 | 305.6714 | 7.9005
54.6809 | 85.483 | 68.6839 | 43.4568 | 99.7347 | 21.2155 | 130.9097 | 8.6149 | 180.4605 | 8.0033 | 233.343 | 8.3949 | 298.7213 | 9.0907
54.6809 | 123.491 | 68.0685 | 54.2491 | 98.3482 | 25.5188 | 128.8326 | 9.6696 | 176.8873 | 8.9738 | 228.9518 | 9.5263 | 293.0996 | 10.1937
54.6809 | 169.879 | 67.5261 | 67.7239 | 97.2723 | 30.0295 | 126.9143 | 10.854 | 174.4276 | 9.9828 | 224.6432 | 11.0284 | 287.5827 | 11.5918
54.6809 | 227.927 | 67.055 | 88.3496 | 96.016 | 36.7793 | 125.2749 | 12.0632 | 171.1444 | 11.2056 | 220.4151 | 12.7685 | 282.1705 | 13.3943
54.7356 | 306.121 | 66.5208 | 117.236 | 95.2508 | 43.0248 | 123.5329 | 13.9533 | 168.4289 | 12.5664 | 216.0503 | 15.1725 | 277.4144 | 15.3246
54.6809 | 429.21 | 66.3215 | 161.273 | 94.1147 | 52.7522 | 121.694 | 16.0121 | 166.2526 | 14.009 | 211.3492 | 18.175 | 273.011 | 17.3944
54.6809 | 520.573 | 65.9907 | 210.406 | 93.2715 | 67.1846 | 120.242 | 18.746 | 163.9417 | 15.4782 | 206.9569 | 22.7964 | 268.677 | 20.0422
54.6809 | 577.046 | 65.9907 | 270.426 | 92.2511 | 85.9113 | 118.6896 | 21.9478 | 161.8238 | 17.4639 | 203.2646 | 28.5099 | 263.094 | 24.2035
54.6809 | 603.001 | 65.9907 | 332.61 | 91.6076 | 104.923 | 117.5089 | 25.3663 | 159.8934 | 19.7051 | 199.6396 | 34.8828 | 259.4359 | 27.7514
|  | 66.0567 | 414.863 | 91.0596 | 126.616 | 116.456 | 29.6125 | 157.9871 | 22.3681 | 196.2737 | 45.9117 | 255.8296 | 32.1076
|  | 66.0567 | 491.241 | 90.6054 | 155.106 | 115.1815 | 35.8364 | 156.2584 | 25.9815 | 193.158 | 59.2357 | 252.2729 | 37.0744
|  | 66.0567 | 566.187 | 90.0634 | 201.552 | 114.2642 | 42.7677 | 154.5485 | 29.2014 | 190.2827 | 75.5941 | 248.7659 | 42.8532
|  | 66.0567 | 608.453 | 89.6142 | 255.7 | 113.3535 | 51.9156 | 152.7051 | 34.3297 | 187.8252 | 94.9425 | 245.798 | 48.4568
|  |  |  | 88.9892 | 336.289 | 112.788 | 61.1606 | 150.8837 | 40.8059 | 185.2134 | 124.234 | 242.8664 | 56.2924
|  |  |  | 88.5453 | 422.398 | 111.8894 | 74.9172 | 148.9345 | 53.4954 | 183.1881 | 159.349 | 239.7298 | 64.4873
|  |  |  | 88.1036 | 513.85 | 111.5543 | 87.0349 | 147.7482 | 64.1018 | 181.7284 | 207.067 | 236.6329 | 76.6593
|  |  |  | 87.9277 | 578.201 | 110.9975 | 105.977 | 146.5708 | 76.4298 | 180.4605 | 258.787 | 234.0442 | 88.7923
|  |  |  | 87.7519 | 609.061 | 110.5543 | 127.506 | 145.2577 | 98.1265 | 179.2015 | 326.025 | 231.4842 | 101.62
[6 empty] | 110.2239 | 173.83 | 144.3889 | 115.491 | 177.9512 | 415.278 | 228.7224 | 122.141
[6 empty] | 109.8938 | 223.638 | 143.2379 | 141.052 | 176.8873 | 498.664 | 226.4469 | 146.807
[6 empty] | 109.6742 | 282.589 | 142.6668 | 170.73 | 176.357 | 559.433 | 224.1934 | 178.23
[6 empty] | 109.2364 | 347.918 | 142.239 | 216.38 | 175.6525 | 606.024 | 221.963 | 209.148
[6 empty] | 108.8003 | 424.515 | 142.0968 | 278.661 |  |  | 220.6356 | 251.642
[6 empty] | 108.4744 | 488.302 | 141.6712 | 359.589 |  |  | 219.3159 | 299.162
[6 empty] | 108.1494 | 569.024 | 141.6712 | 461.25 |  |  | 218.2211 | 362.115
[6 empty] | 108.0414 | 602.399 | 141.6712 | 569.594 |  |  | 216.9158 | 446.724
[8 empty] | 141.5301 | 601.797 |  |  | 216.0503 | 553.867
[12 empty] | 215.1882 | 601.195