## 690-9-2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Main Interrupter Speed (TCC 690-9-2) | [9 empty] | Main Interrupter Speed (TCC 690-9-2) | [9 empty] | Main Interrupter Speed (TCC 690-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.
100A |  | 150A |  | 200A |  | 250A |  | 300A |  | 350A |  | 400A |  | 450A |  | 500A |  | 600A |  | 700A |  | 800A
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
25000 | 0.0846 | 25000 | 0.0846 | 25000 | 0.0846 | 25000 | 0.0846 | 25000 | 0.0846 | 25000 | 0.0846 | 25000 | 0.0885 | 25000 | 0.0905 | 25000 | 0.094 | 25000 | 0.095 | 25000 | 0.096 | 25000 | 0.1
16000 | 0.0846 | 16000 | 0.0846 | 16000 | 0.0846 | 16000 | 0.0846 | 16000 | 0.0846 | 16000 | 0.0846 | 16000 | 0.0895 | 16000 | 0.0905 | 16000 | 0.0923 | 16000 | 0.0939 | 16000 | 0.0975 | 16000 | 0.1046
15270.106 | 0.0846 | 8500 | 0.08472 | 15270.106 | 0.0846 | 14000.247 | 0.0846 | 14891.846 | 0.0846 | 13699.59 | 0.08472 | 14918.188 | 0.0895 | 11431.828 | 0.0911 | 15472.571 | 0.0926 | 15473.506 | 0.0942 | 15096.55 | 0.0979 | 15363.847 | 0.1051
12406.845 | 0.0846 | 4320.05 | 0.08508 | 12406.845 | 0.08472 | 12212.246 | 0.08472 | 12990.163 | 0.0846 | 11946.713 | 0.0846 | 12983.748 | 0.0896 | 12610.217 | 0.0907 | 14322.568 | 0.0931 | 13939.216 | 0.0951 | 13416.61 | 0.0997 | 13413.765 | 0.1076
9528.171 | 0.0846 | 3974.242 | 0.08568 | 9528.171 | 0.08472 | 10630.395 | 0.0846 | 11155.44 | 0.08472 | 10705.09 | 0.08448 | 11806.774 | 0.0898 | 13751.294 | 0.0906 | 13093.028 | 0.0936 | 12543.954 | 0.0966 | 11898.73 | 0.1016 | 11338.204 | 0.1117
7565.874 | 0.0846 | 3721.514 | 0.08592 | 7565.874 | 0.0852 | 9647.669 | 0.0846 | 9904.958 | 0.08472 | 9693.287 | 0.0846 | 10691.74 | 0.0898 | 14716.542 | 0.0906 | 12006.575 | 0.0945 | 11300.147 | 0.0982 | 10519.58 | 0.1044 | 9961.293 | 0.1156
6001.441 | 0.0846 | 3409.364 | 0.08724 | 6001.441 | 0.08592 | 7938.079 | 0.0852 | 8640.099 | 0.08508 | 8934.452 | 0.08508 | 9938.094 | 0.0898 | 10907.338 | 0.0913 | 11033.281 | 0.0953 | 10094.985 | 0.1 | 9707.025 | 0.1066 | 8936.271 | 0.1191
5004.905 | 0.0846 | 3024.032 | 0.0894 | 5474.905 | 0.0858 | 6795.504 | 0.08556 | 7948.483 | 0.08568 | 8352.64 | 0.08616 | 9227.931 | 0.0908 | 9734.483 | 0.0926 | 10086.115 | 0.0964 | 9295.631 | 0.102 | 8892.008 | 0.1091 | 7892.145 | 0.1245
4126.571 | 0.08544 | 2776.17 | 0.09096 | 5126.571 | 0.08604 | 6090.584 | 0.08664 | 7443.027 | 0.08592 | 7334.596 | 0.08784 | 8470.656 | 0.092 | 8954.714 | 0.094 | 9326.722 | 0.0978 | 8149.621 | 0.1053 | 8162.447 | 0.1117 | 6962.742 | 0.1308
2397.696 | 0.0864 | 2488.218 | 0.09348 | 5000 | 0.0864 | 5709.187 | 0.08748 | 6750.729 | 0.08724 | 6570.906 | 0.08952 | 7543.591 | 0.0946 | 8332.521 | 0.0952 | 8437.535 | 0.0997 | 7356.886 | 0.1087 | 7461.519 | 0.1152 | 6170.942 | 0.1378
2285.327 | 0.08688 | 2244.131 | 0.09612 | 4570.654 | 0.08688 | 5379.656 | 0.08868 | 5900.064 | 0.0894 | 5925.029 | 0.09156 | 6788.506 | 0.0964 | 7538.119 | 0.0973 | 7721.259 | 0.1019 | 6620.49 | 0.1122 | 6778.19 | 0.1192 | 5482.725 | 0.148
2212.586 | 0.08712 | 2049.478 | 0.09912 | 4425.171 | 0.08712 | 4950.454 | 0.09 | 5490.34 | 0.09096 | 5501.29 | 0.0936 | 6109.003 | 0.0989 | 6948.777 | 0.099 | 7162.309 | 0.1039 | 5951.586 | 0.1169 | 6241.579 | 0.1233 | 4940.639 | 0.1575
2100.108 | 0.08784 | 1863.917 | 0.10224 | 4200.216 | 0.08784 | 4603.071 | 0.09156 | 4966.435 | 0.09348 | 4970.928 | 0.09708 | 5660.627 | 0.1007 | 6385.485 | 0.1012 | 6418.894 | 0.1069 | 5450 | 0.1212 | 5658.145 | 0.1285 | 4448.85 | 0.17052
1999.598 | 0.08892 | 1682.826 | 0.10632 | 3999.196 | 0.08892 | 4222.232 | 0.09372 | 4488.262 | 0.09612 | 4515.231 | 0.10068 | 5169.038 | 0.10368 | 5898.557 | 0.1033 | 5892.404 | 0.1099 | 4993.949 | 0.1266 | 5150.713 | 0.1351 | 4079.537 | 0.1854
1880.207 | 0.09024 | 1491.074 | 0.11184 | 3760.414 | 0.09024 | 3842.005 | 0.09564 | 4070.956 | 0.09912 | 4157.41 | 0.1038 | 4730.008 | 0.10692 | 5386.563 | 0.1062 | 5448.76 | 0.1126 | 4500 | 0.13416 | 4772.749 | 0.14208 | 3748.702 | 0.20388
1756.91 | 0.09168 | 1339.206 | 0.11844 | 3513.821 | 0.09168 | 3460.546 | 0.09912 | 3727.834 | 0.10224 | 3721.439 | 0.10884 | 4305.728 | 0.11136 | 4873.021 | 0.11016 | 4970.617 | 0.1164 | 4050 | 0.14316 | 4350 | 0.15144 | 3433.924 | 0.22704
1639.988 | 0.09348 | 1190.327 | 0.12588 | 3279.975 | 0.09348 | 3163.65 | 0.10236 | 3365.653 | 0.10632 | 3412.23 | 0.11328 | 3956.514 | 0.11556 | 4459.342 | 0.11448 | 4693.327 | 0.11952 | 3755 | 0.15432 | 4055 | 0.15984 | 3148.863 | 0.25404
1514.954 | 0.0954 | 1083.684 | 0.1344 | 3029.909 | 0.0954 | 2898.266 | 0.10596 | 2982.149 | 0.11184 | 3122.18 | 0.11928 | 3669.953 | 0.11988 | 4114.996 | 0.11964 | 4349.03 | 0.12468 | 3501.489 | 0.16296 | 3800 | 0.171 | 2973.129 | 0.2748
1384.928 | 0.0984 | 1001.106 | 0.14232 | 2769.855 | 0.0984 | 2688.586 | 0.10932 | 2678.413 | 0.11844 | 2889.817 | 0.12444 | 3361.756 | 0.12588 | 3849.111 | 0.12348 | 3988.15 | 0.13068 | 3200.748 | 0.17748 | 3514.957 | 0.18612 | 2706.467 | 0.31452
1254.226 | 0.10176 | 920.97 | 0.1524 | 2508.453 | 0.10176 | 2460.485 | 0.11352 | 2380.654 | 0.12588 | 2646.939 | 0.13188 | 3108.518 | 0.13152 | 3585.407 | 0.12864 | 3676.35 | 0.13704 | 2959.639 | 0.19344 | 3290 | 0.20004 | 2505.226 | 0.35604
1098.559 | 0.10752 | 849.904 | 0.16236 | 2197.118 | 0.10752 | 2284.858 | 0.11808 | 2167.368 | 0.1344 | 2437.176 | 0.1398 | 2901.497 | 0.138 | 3300 | 0.135 | 3445.993 | 0.14436 | 2719.599 | 0.21516 | 3020 | 0.22044 | 2278.151 | 0.41364
973.32 | 0.11352 | 793.371 | 0.17376 | 1946.641 | 0.11352 | 2119.555 | 0.123 | 2002.211 | 0.14232 | 2237.011 | 0.14916 | 2627.479 | 0.14808 | 3055 | 0.1434 | 3146.881 | 0.1542 | 2491.211 | 0.23916 | 2837.731 | 0.24156 | 2131.5206 | 0.458
870.496 | 0.12012 | 729.103 | 0.19188 | 1740.992 | 0.12012 | 1962.115 | 0.12852 | 1830.54 | 0.1524 | 2070.525 | 0.159 | 2419.427 | 0.1572 | 2808.5 | 0.15252 | 2906.914 | 0.1644 | 2303.551 | 0.26568 | 2626.752 | 0.26712 | 1999.9936 | 0.5237
775.292 | 0.12876 | 679.896 | 0.20736 | 1550.583 | 0.12876 | 1848.862 | 0.13368 | 1702.807 | 0.16236 | 1924.458 | 0.171 | 2186.365 | 0.1728 | 2632.522 | 0.16116 | 2716.252 | 0.17496 | 2105.7 | 0.3042 | 2459.543 | 0.2946 | 1890.3489 | 0.5889
681.907 | 0.14052 | 636.66 | 0.22668 | 1363.814 | 0.14052 | 1740.331 | 0.13956 | 1596.742 | 0.17376 | 1768.25 | 0.18588 | 2055.729 | 0.18456 | 2444.501 | 0.1722 | 2540.745 | 0.1866 | 1940.989 | 0.34584 | 2271.932 | 0.3348 | 1794.1935 | 0.6655
620.783 | 0.15288 | 593.074 | 0.24912 | 1241.566 | 0.15288 | 1611.059 | 0.14784 | 1458.206 | 0.19188 | 1645.225 | 0.2004 | 1924.842 | 0.19776 | 2332.348 | 0.1806 | 2369.149 | 0.2034 | 1825.015 | 0.38004 | 2142.913 | 0.36744 | 1706.4883 | 0.7465
552.312 | 0.17028 | 553.624 | 0.27504 | 1104.625 | 0.17028 | 1486.73 | 0.15912 | 1359.792 | 0.20736 | 1532.361 | 0.21936 | 1815.511 | 0.21384 | 2183.925 | 0.19308 | 2186.205 | 0.22524 | 1698.145 | 0.42696 | 2004.409 | 0.40908 | 1617.9944 | 0.8515
497.586 | 0.19212 | 513.04 | 0.30552 | 995.172 | 0.19212 | 1335.289 | 0.17628 | 1273.321 | 0.22668 | 1439.222 | 0.24 | 1682.26 | 0.23364 | 2075.046 | 0.20484 | 2006.888 | 0.25236 | 1575.152 | 0.48168 | 1847.653 | 0.46944 | 1540.5104 | 0.975
445.484 | 0.21888 | 489.519 | 0.33396 | 890.968 | 0.21888 | 1232.242 | 0.19272 | 1186.147 | 0.24912 | 1357.408 | 0.25944 | 1590.025 | 0.25272 | 1947.056 | 0.22128 | 1869.396 | 0.2802 | 1515.8858 | 0.5288 | 1778.1852 | 0.5138 | 1466.7367 | 1.1057
408.526 | 0.24816 | 459.826 | 0.3678 | 817.051 | 0.24816 | 1139.522 | 0.21228 | 1100.249 | 0.27504 | 1276.236 | 0.2832 | 1495.021 | 0.27384 | 1836.52 | 0.24072 | 1728.647 | 0.31308 | 1444.7928 | 0.5864 | 1668.4723 | 0.5829 | 1395.0387 | 1.2662
372.294 | 0.27756 | 431.034 | 0.40776 | 744.589 | 0.27756 | 1069.279 | 0.23028 | 1026.08 | 0.30552 | 1181.254 | 0.3168 | 1411.577 | 0.30108 | 1698.247 | 0.2676 | 1563.842 | 0.36288 | 1355.6312 | 0.6781 | 1560.6338 | 0.6788 | 1333.7907 | 1.4794
329.508 | 0.3336 | 419.6742 | 0.4297 | 659.016 | 0.3336 | 990.886 | 0.255 | 979.038 | 0.33396 | 1108.297 | 0.35112 | 1334.183 | 0.32568 | 1576.954 | 0.29736 | 1467.384 | 0.40128 | 1262.7098 | 0.8051 | 1476.6257 | 0.7716 | 1287.2717 | 1.6853
295.314 | 0.39684 | 391.3492 | 0.4914 | 590.627 | 0.39684 | 926.805 | 0.27924 | 919.652 | 0.3678 | 1044.202 | 0.38388 | 1272.939 | 0.3522 | 1487.429 | 0.32628 | 1365.427 | 0.45636 | 1176.1563 | 0.9571 | 1385.5193 | 0.8903 | 1229.4711 | 1.9385
262.194 | 0.48984 | 366.8456 | 0.5582 | 524.387 | 0.48984 | 867.671 | 0.30432 | 887.0477 | 0.3862 | 978.687 | 0.42876 | 1191.892 | 0.38928 | 1365.427 | 0.37236 | 1332.0967 | 0.4729 | 1111.6699 | 1.1101 | 1298.8734 | 1.0396 | 1181.6442 | 2.2773
242.5434 | 0.5806 | 350.7581 | 0.6238 | 485.0857 | 0.5806 | 819.561 | 0.33396 | 839.3473 | 0.4297 | 920.162 | 0.48216 | 1176.1563 | 0.3977 | 1254.741 | 0.42408 | 1259.0974 | 0.5324 | 1043.0673 | 1.3124 | 1217.2776 | 1.2686 | 1139.2414 | 2.5777
224.5188 | 0.6995 | 333.2835 | 0.7005 | 449.0387 | 0.6995 | 777.916 | 0.36348 | 782.6995 | 0.4914 | 879.9065 | 0.5301 | 1132.7635 | 0.4295 | 1198.424 | 0.46176 | 1180.2032 | 0.6096 | 987.9386 | 1.529 | 1151.7528 | 1.4884 | 1093.7828 | 2.9924
205.678 | 0.8622 | 313.0677 | 0.8073 | 411.356 | 0.8622 | 744.0906 | 0.3866 | 735.8912 | 0.5582 | 836.8536 | 0.5924 | 1079.6368 | 0.47 | 1123.332 | 0.52176 | 1124.882 | 0.6855 | 941.6055 | 1.7692 | 1084.0808 | 1.7988 | 1053.4326 | 3.5892
190.1955 | 1.0602 | 295.6151 | 0.9388 | 380.391 | 1.0602 | 698.2239 | 0.4352 | 701.5162 | 0.6238 | 804.2705 | 0.6433 | 1011.9538 | 0.5339 | 1054.3973 | 0.614 | 1065.46 | 0.7737 | 908.7617 | 1.9996 | 1035.408 | 2.1527 | 1016.6915 | 4.2569
173.1466 | 1.3788 | 281.182 | 1.0615 | 346.2943 | 1.3788 | 655.7551 | 0.4904 | 666.567 | 0.7005 | 768.9264 | 0.708 | 966.5106 | 0.5862 | 1008.1236 | 0.6815 | 1010.2301 | 0.8792 | 877.9793 | 2.263 | 988.9209 | 2.5403 | 981.2319 | 5.0077
155.3409 | 1.9054 | 262.9 | 1.284 | 313.918 | 1.9054 | 626.4478 | 0.5379 | 626.1354 | 0.8073 | 730.5408 | 0.8029 | 920.2204 | 0.657 | 961.8719 | 0.7592 | 958.8645 | 1.0089 | 848.2397 | 2.6074 | 944.5205 | 3.0651 | 955.9506 | 5.923
148.06 | 2.3296 | 248.622 | 1.4884 | 296.1211 | 2.3296 | 593.9945 | 0.6023 | 591.2302 | 0.9388 | 701.3633 | 0.8918 | 872.4958 | 0.7377 | 920.6186 | 0.8496 | 914.8722 | 1.1337 | 821.2204 | 2.9986 | 906.8356 | 3.6081 | 932.2929 | 6.9846
138.4966 | 2.9808 | 236.5 | 1.7297 | 276.9921 | 2.9808 | 564.9886 | 0.6734 | 562.3629 | 1.0615 | 667.744 | 1.0031 | 839.4276 | 0.817 | 882.0559 | 0.9541 | 865.6395 | 1.328 | 788.4481 | 3.4602 | 876.1258 | 4.3245 | 912.0738 | 8.3334
133.2507 | 3.554 | 226.1116 | 2.0489 | 266.5014 | 3.554 | 539.0836 | 0.7634 | 524.9706 | 1.284 | 643.7607 | 1.1036 | 803.4081 | 0.9099 | 848.6434 | 1.0482 | 816.497 | 1.5471 | 757.7746 | 4.1558 | 845.5711 | 5.1304 | 900.7163 | 9.8916
127.006 | 4.448 | 216.4217 | 2.3904 | 254.012 | 4.448 | 514.9903 | 0.8546 | 499.4451 | 1.4884 | 622.5868 | 1.2094 | 764.1315 | 1.0159 | 815.6456 | 1.1589 | 773.3649 | 1.8755 | 734.404 | 4.8479 | 819.4989 | 6.2693 | 889.5018 | 11.3534
122.5796 | 5.4702 | 208.8812 | 2.7549 | 242.9581 | 5.4702 | 490.7815 | 0.968 | 474.2309 | 1.7297 | 597.7202 | 1.345 | 735.9396 | 1.1323 | 786.3878 | 1.2963 | 741.7443 | 2.1599 | 713.2422 | 5.8803 | 801.7273 | 7.3085 | 880 | 13.3936
121 | 5.9273 | 199.9294 | 3.2803 | 231.957 | 7.0626 | 464.387 | 1.1163 | 452.2243 | 2.0489 | 573.848 | 1.5133 | 686.9269 | 1.3709 | 750.3089 | 1.4656 | 709.192 | 2.5726 | 694.8634 | 7.0372 | 789.2698 | 8.503 | 880 | 16.5685
115.72 | 7.83 | 190.7642 | 3.9898 | 224.2999 | 9.276 | 440.7887 | 1.2894 | 432.8434 | 2.3904 | 556.7166 | 1.6891 | 660.2035 | 1.5043 | 727.9393 | 1.6084 | 685.1823 | 2.9707 | 674.8401 | 8.5389 | 778.6295 | 9.9145 | 880 | 19.5485
113.52 | 9.43 | 183.5427 | 4.9208 | 220 | 13.4837 | 414.4811 | 1.5354 | 417.7635 | 2.7549 | 537.8428 | 1.876 | 640.5102 | 1.663 | 709.192 | 1.7895 | 662.6763 | 3.4169 | 664.3527 | 10.3734 | 772.2 | 11.7204 | 880 | 23.2854
111.32 | 11.43 | 180.4 | 5.2899 | 220 | 18.2492 | 393.8308 | 1.79 | 399.8599 | 3.2803 | 523.9729 | 2.0925 | 614.3071 | 1.9008 | 676.654 | 2.0651 | 644.9355 | 3.8214 | 661.1 | 11.9824 | 770 | 13.6392 | 880 | 27.0734
110 | 13.43 | 177.1 | 6.03 | 220 | 25.0176 | 376.1648 | 2.136 | 381.5273 | 3.9898 | 504.625 | 2.3713 | 589.7925 | 2.196 | 660.605 | 2.2866 | 628.9822 | 4.3739 | 660 | 13.9588 | 770 | 15.7397 | 880 | 33.7824
110 | 600 | 172.7 | 7.03 | 220 | 38.5645 | 361.9242 | 2.4484 | 365.9854 | 4.9208 | 492.1246 | 2.646 | 574.5949 | 2.4572 | 637.5743 | 2.6292 | 612.7825 | 5.0227 | 660 | 18.1645 | 770 | 18.6887 | 880 | 41.1459
|  | 170.83 | 7.83 | 220 | 74.296 | 350.4446 | 2.7262 | 353.2078 | 5.9758 | 476.4364 | 3.0027 | 555.7112 | 2.7875 | 622.4515 | 2.9001 | 595.1352 | 5.817 | 660 | 21.5915 | 770 | 21.1189 | 880 | 50.7541
|  | 168.3 | 9.43 | 220 | 126.7847 | 340.7151 | 3.0904 | 343.3595 | 7.033 | 458.3645 | 3.5243 | 539.1353 | 3.1993 | 603.8945 | 3.3324 | 580.4128 | 6.9097 | 660 | 25.4775 | 770 | 24.8934 | 880 | 66.9098
|  | 166.98 | 10.43 | 220 | 221.458 | 329.8394 | 3.4856 | 337.7077 | 8.2261 | 448.4139 | 3.9219 | 521.9621 | 3.688 | 585.8908 | 3.8178 | 571.9934 | 8.123 | 660 | 30.5432 | 770 | 29.9374 | 880 | 80.1366
|  | 166.32 | 11.43 | 220 | 313.1658 | 322.3572 | 3.9565 | 333.883 | 9.5821 | 435.9377 | 4.434 | 507.9822 | 4.1554 | 569.0168 | 4.4022 | 564.2857 | 9.2537 | 660 | 35.4396 | 770 | 35.1049 | 880 | 93.7774
|  | 165 | 13.43 | 220 | 458.0831 | 315.0444 | 4.4215 | 332.772 | 10.9644 | 426.9199 | 4.9144 | 495.4092 | 4.7218 | 556.1006 | 5.0397 | 556.6814 | 10.6989 | 660 | 43.5779 | 770 | 42.5335 | 880 | 109.1635
|  | 165 | 600 | 220 | 600 | 300.9127 | 5.6641 | 330 | 13.4075 | 415.4755 | 5.6513 | 484.6633 | 5.3549 | 544.0446 | 5.5621 | 551.4762 | 12.8483 | 660 | 51.3185 | 770 | 50.78 | 880 | 132.134
[6 empty] | 288.9183 | 7.1223 | 330 | 15.8528 | 409.013 | 6.4721 | 475.6389 | 6.1054 | 534.4768 | 6.4428 | 550 | 15.382 | 660 | 62.3783 | 770 | 58.1213 | 880 | 160.7854
[6 empty] | 281.4812 | 8.6613 | 330 | 18.1234 | 398.0493 | 7.4597 | 465.1955 | 6.8672 | 528.3861 | 7.2549 | 550 | 18.9478 | 660 | 78.5097 | 770 | 78.5926 | 880 | 192.9854
[6 empty] | 277.2 | 10.4901 | 330 | 21.544 | 392.2666 | 8.1664 | 457.6693 | 7.9889 | 519.0449 | 8.512 | 550 | 22.8554 | 660 | 102.9664 | 770 | 101.0292 | 880 | 238.3297
[6 empty] | 276.1 | 12.0925 | 330 | 25.1563 | 389.8147 | 9.0731 | 451.132 | 9.5421 | 507.6885 | 9.8832 | 550 | 28.1573 | 660 | 129.7365 | 770 | 123.7196 | 880 | 288.1832
[6 empty] | 275 | 13.6642 | 330 | 30.1282 | 386.5697 | 10.339 | 446.7529 | 11.0445 | 502.3722 | 10.808 | 550 | 35.0585 | 660 | 165.5519 | 770 | 148.6568 | 880 | 354.7742
[6 empty] | 275 | 15.3272 | 330 | 34.8125 | 385.99 | 11.4998 | 440 | 13.5033 | 498.3473 | 12.6567 | 550 | 41.6745 | 660 | 205.756 | 770 | 184.7572 | 880 | 429.8952
[6 empty] | 275 | 19.8851 | 330 | 43.3093 | 385 | 13.0916 | 440 | 15.6149 | 495 | 14.7757 | 550 | 50.2237 | 660 | 259.5322 | 770 | 221.0653 | 880 | 514.9119
[6 empty] | 275 | 25.2893 | 330 | 53.5416 | 385 | 14.9672 | 440 | 17.7371 | 495 | 16.98 | 550 | 61.041 | 660 | 319.5142 | 770 | 259.8063 | 880 | 572.2212
[6 empty] | 275 | 31.1625 | 330 | 64.2658 | 385 | 18.1724 | 440 | 19.9371 | 495 | 19.4318 | 550 | 72.7945 | 660 | 392.5312 | 770 | 316.8277 | 880 | 600
[6 empty] | 275 | 39.1375 | 330 | 78.9512 | 385 | 20.3868 | 440 | 22.6479 | 495 | 23.3923 | 550 | 89.4142 | 660 | 480.2045 | 770 | 379.0946
[6 empty] | 275 | 46.2861 | 330 | 98.3341 | 385 | 24.238 | 440 | 27.0057 | 495 | 27.5738 | 550 | 106.5215 | 660 | 541.6053 | 770 | 462.7885
[6 empty] | 275 | 55.031 | 330 | 121.4474 | 385 | 27.2501 | 440 | 30.8088 | 495 | 32.8138 | 550 | 126.6358 | 660 | 600 | 770 | 538.1862
[6 empty] | 275 | 65.3602 | 330 | 154.0064 | 385 | 31.3568 | 440 | 35.483 | 495 | 37.7945 | 550 | 166.592 |  |  | 770 | 600
[6 empty] | 275 | 78.6186 | 330 | 187.4189 | 385 | 38.1192 | 440 | 43.1704 | 495 | 44.554 | 550 | 224.0671
[6 empty] | 275 | 94.8677 | 330 | 238.6744 | 385 | 47.1807 | 440 | 47.971 | 495 | 50.4596 | 550 | 299.79
[6 empty] | 275 | 108.4767 | 330 | 292.6142 | 385 | 55.2777 | 440 | 55.9555 | 495 | 57.8156 | 550 | 389.4327
[6 empty] | 275 | 129.7986 | 330 | 366.0147 | 385 | 64.6286 | 440 | 63.9075 | 495 | 72.46 | 550 | 473.8551
[6 empty] | 275 | 150.3122 | 330 | 459.7667 | 385 | 76.6067 | 440 | 73.6863 | 495 | 91.8761 | 550 | 554.5089
[6 empty] | 275 | 181.5764 | 330 | 535.2594 | 385 | 88.1597 | 440 | 88.4368 | 495 | 111.9181 | 550 | 600
[6 empty] | 275 | 223.7887 | 330 | 600 | 385 | 99.8611 | 440 | 102.7267 | 495 | 131.2513
[6 empty] | 275 | 256.168 |  |  | 385 | 116.8812 | 440 | 119.4523 | 495 | 154.2504
[6 empty] | 275 | 306.8513 |  |  | 385 | 140.6123 | 440 | 134.7169 | 495 | 196.4198
[6 empty] | 275 | 369.1192 |  |  | 385 | 161.8218 | 440 | 151.4527 | 495 | 231.5732
[6 empty] | 275 | 426.5627 |  |  | 385 | 183.3036 | 440 | 175.0029 | 495 | 275.6247
[6 empty] | 275 | 497.1276 |  |  | 385 | 214.5498 | 440 | 201.7896 | 495 | 318.8405
[6 empty] | 275 | 572.0727 |  |  | 385 | 258.9355 | 440 | 234.402 | 495 | 377.4975
[6 empty] | 275 | 600 |  |  | 385 | 307.2671 | 440 | 266.8819 | 495 | 445.5337
[10 empty] | 385 | 381.5666 | 440 | 307.4101 | 495 | 508.3693
[10 empty] | 385 | 435.8933 | 440 | 346.3345 | 495 | 579.4557
[10 empty] | 385 | 493.2433 | 440 | 403.5866 | 495 | 600
[10 empty] | 385 | 547.6258 | 440 | 464.3868
[10 empty] | 385 | 600 | 440 | 523.1896
[12 empty] | 440 | 600
S&C Vista Underground Distribution Switchgear Overcurrent Control
Main Interrupter Speed (TCC 690-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: Curves are plotted to maximum test points. All variations are minus.