## 153_214
S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV) | [9 empty] | S&C Power Fuses - Type SMU-40 (4.8 kV)
Standard Speed (TCC 153-2-1-4) | [9 empty] | Standard Speed (TCC 153-2-1-4) | [9 empty] | Standard Speed (TCC 153-2-1-4) | [9 empty] | Standard Speed (TCC 153-2-1-4) | [9 empty] | Standard Speed (TCC 153-2-1-4)
Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated June 17, 1991
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3E |  | 5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015793 | 29999.2 | 0.015904 | 29999.2 | 0.015904 | 29999.2 | 0.015904 | 29999.2 | 0.016 | 29999.2 | 0.016096 | 29999.2 | 0.016888 | 29999.2 | 0.017194 | 29999.2 | 0.017402 | 29999.2 | 0.017594 | 29999.2 | 0.018203 | 29999.2 | 0.023989 | 29999.2 | 0.025702 | 29999.2 | 0.028292 | 29999.2 | 0.031899 | 29999.2 | 0.038382
23504 | 0.016888 | 25872.2 | 0.016504 | 28621.8 | 0.016 | 28593.2 | 0.016 | 28422.2 | 0.016096 | 25032.4 | 0.016603 | 26527.2 | 0.016405 | 26132.2 | 0.016504 | 28822.9 | 0.016 | 28479.1 | 0.016096 | 26713.5 | 0.016405 | 28111.3 | 0.016307 | 27389.8 | 0.016504 | 26158.4 | 0.016888 | 25309.2 | 0.0177 | 24414.3 | 0.018294 | 27417.2 | 0.017896 | 23015.5 | 0.019309 | 27554.6 | 0.018795 | 26054 | 0.025295 | 25640.4 | 0.027788 | 25082.5 | 0.031995 | 27971 | 0.033703 | 27859.4 | 0.041413
18086.6 | 0.018203 | 19909 | 0.0177 | 22002.8 | 0.017194 | 21980.8 | 0.017298 | 21871.2 | 0.017298 | 19262.7 | 0.017896 | 20392.6 | 0.017594 | 20109 | 0.0177 | 22179.5 | 0.017298 | 21915 | 0.017402 | 20535.8 | 0.0177 | 21631.9 | 0.017594 | 21055.7 | 0.017896 | 20129.2 | 0.018404 | 19475.7 | 0.019098 | 18768.3 | 0.019997 | 21076.7 | 0.019582 | 17710.7 | 0.021706 | 21203.6 | 0.021001 | 20048.8 | 0.028806 | 19710.9 | 0.032904 | 22809.3 | 0.034315 | 24832.9 | 0.037397 | 26210.8 | 0.044194
13903.9 | 0.019582 | 15304.8 | 0.019098 | 16931.4 | 0.018608 | 16914.5 | 0.018608 | 16830.1 | 0.018608 | 14808 | 0.019309 | 15692.3 | 0.019003 | 15474.1 | 0.019098 | 17067.4 | 0.018608 | 16846.9 | 0.018701 | 15802.5 | 0.019213 | 16629.4 | 0.019098 | 16202.6 | 0.019503 | 15489.6 | 0.020198 | 14971.8 | 0.020792 | 14442.4 | 0.022412 | 16218.8 | 0.022012 | 13628.6 | 0.024993 | 16316.4 | 0.0244 | 15412.4 | 0.033906 | 19128.3 | 0.033602 | 20250.3 | 0.038114 | 21871.2 | 0.042419 | 24463.2 | 0.047923
10699.2 | 0.021107 | 11777.2 | 0.020503 | 13028.9 | 0.019997 | 13015.9 | 0.019997 | 12938 | 0.019997 | 11394.9 | 0.020792 | 12075.4 | 0.020503 | 11895.6 | 0.020606 | 13120.4 | 0.020097 | 12963.9 | 0.020198 | 12148.1 | 0.020792 | 12796.5 | 0.020792 | 12468 | 0.021404 | 11907.5 | 0.022502 | 11521 | 0.023187 | 11113.6 | 0.025702 | 12480.5 | 0.025295 | 10476.9 | 0.030102 | 12543.1 | 0.029417 | 14956.8 | 0.034625 | 18213.6 | 0.034904 | 17290.7 | 0.044282 | 19339.9 | 0.048404 | 22537.3 | 0.052699
8233.18 | 0.022705 | 9062.75 | 0.0221 | 10015.8 | 0.021511 | 10005.8 | 0.021511 | 9955.97 | 0.021511 | 8768.56 | 0.022412 | 9282.89 | 0.0221 | 9153.83 | 0.0223 | 10096.3 | 0.021706 | 9965.93 | 0.021902 | 9348.1 | 0.022614 | 9847.06 | 0.022796 | 9584.74 | 0.023798 | 9162.99 | 0.025498 | 8865.55 | 0.026591 | 8543.52 | 0.030771 | 9594.33 | 0.030404 | 10045.9 | 0.031081 | 11406.3 | 0.031677 | 13987.6 | 0.036401 | 17118.7 | 0.036693 | 15122.3 | 0.051397 | 16999.3 | 0.05652 | 21118.9 | 0.057088
6329.19 | 0.0244 | 6966.92 | 0.023798 | 7707.34 | 0.023094 | 7699.63 | 0.023094 | 7661.23 | 0.023187 | 6740.76 | 0.024109 | 7143.29 | 0.023798 | 7036.94 | 0.024109 | 7761.48 | 0.02349 | 7668.9 | 0.023798 | 7193.46 | 0.024794 | 7569.85 | 0.025295 | 7375.57 | 0.026886 | 7051.02 | 0.029594 | 6815.32 | 0.031804 | 8332.58 | 0.031393 | 9357.45 | 0.030988 | 9320.09 | 0.033301 | 10126.6 | 0.035502 | 12418.3 | 0.040229 | 16332.7 | 0.038114 | 12681.8 | 0.063726 | 15001.8 | 0.066592 | 19671.5 | 0.062589
4870.38 | 0.026222 | 5361.12 | 0.0256 | 5924.95 | 0.024893 | 5924.95 | 0.024893 | 5889.51 | 0.024993 | 5187.09 | 0.026013 | 5491.34 | 0.025805 | 5415 | 0.026222 | 5972.54 | 0.025498 | 5901.3 | 0.026117 | 5529.92 | 0.027401 | 5825.08 | 0.028491 | 5675.58 | 0.030988 | 5420.42 | 0.035502 | 6713.85 | 0.032091 | 7784.8 | 0.033201 | 9126.41 | 0.031677 | 8569.19 | 0.035787 | 8646.66 | 0.041662 | 10937.2 | 0.045222 | 15505.1 | 0.039829 | 11135.8 | 0.075686 | 13425.7 | 0.077369 | 18213.6 | 0.069379
3744.07 | 0.028207 | 4121.32 | 0.027484 | 4559.32 | 0.026778 | 4554.76 | 0.026886 | 4532.04 | 0.026993 | 3987.53 | 0.028095 | 4225.65 | 0.028011 | 4166.9 | 0.028605 | 4595.94 | 0.027899 | 4536.58 | 0.028806 | 4255.33 | 0.030679 | 4482.46 | 0.032805 | 4363.06 | 0.036988 | 5339.72 | 0.036002 | 6463.51 | 0.033102 | 7229.52 | 0.035431 | 8803.71 | 0.032609 | 7792.59 | 0.039393 | 7562.28 | 0.048793 | 9671.4 | 0.051192 | 14763.7 | 0.041662 | 9442.05 | 0.096215 | 11671.7 | 0.095353 | 16897.6 | 0.077292
2881.1 | 0.030404 | 3171.4 | 0.029594 | 3508.45 | 0.028893 | 3504.94 | 0.029008 | 3483.97 | 0.029212 | 3068.45 | 0.030526 | 3251.68 | 0.030618 | 3203.27 | 0.031487 | 3533.09 | 0.030679 | 3490.95 | 0.032285 | 3274.53 | 0.035219 | 3445.86 | 0.038923 | 4306.7 | 0.037397 | 5202.68 | 0.036583 | 6062.81 | 0.034904 | 6680.37 | 0.038114 | 8458.51 | 0.033804 | 7086.37 | 0.043711 | 6341.86 | 0.061105 | 8500.91 | 0.059418 | 13931.7 | 0.044106 | 8086.31 | 0.12256 | 10351.9 | 0.11508 | 15802.5 | 0.085335
2217.04 | 0.032707 | 2440.43 | 0.031899 | 2697.09 | 0.031174 | 2694.39 | 0.031299 | 2680.95 | 0.031677 | 2361.21 | 0.033301 | 2499.71 | 0.033602 | 2464.95 | 0.035219 | 2718.75 | 0.034315 | 2686.32 | 0.036877 | 2517.26 | 0.041496 | 3397.95 | 0.039314 | 4179.42 | 0.038305 | 5028.76 | 0.037697 | 5704.03 | 0.036803 | 6172.93 | 0.04133 | 8134.98 | 0.034904 | 6405.6 | 0.048891 | 5568.76 | 0.073156 | 7502.02 | 0.069588 | 13107.3 | 0.046927 | 6946.05 | 0.1569 | 8681.31 | 0.15348 | 14587.6 | 0.096312
1704.33 | 0.035114 | 1876.06 | 0.034418 | 2075.44 | 0.033703 | 2073.36 | 0.034008 | 2063.02 | 0.034522 | 1815.16 | 0.036583 | 1923.55 | 0.037509 | 1896.81 | 0.040028 | 2092.11 | 0.039118 | 2065.09 | 0.043276 | 2487.24 | 0.041871 | 3277.8 | 0.04031 | 3896.87 | 0.040512 | 4788.29 | 0.039197 | 5409.59 | 0.038613 | 5568.76 | 0.045906 | 7761.48 | 0.036474 | 5813.44 | 0.055124 | 4721.72 | 0.093559 | 6713.85 | 0.080527 | 12233.4 | 0.050582 | 6111.5 | 0.19551 | 7615.4 | 0.19144 | 13683.2 | 0.10623
1311.5 | 0.037811 | 1443.65 | 0.03721 | 1597.07 | 0.036474 | 1595.48 | 0.036988 | 1585.93 | 0.037886 | 1396.78 | 0.040633 | 1480.19 | 0.042376 | 1458.16 | 0.046693 | 1608.29 | 0.045722 | 2034.34 | 0.043711 | 2428.25 | 0.042589 | 3161.9 | 0.041496 | 3582.9 | 0.043492 | 4554.76 | 0.040919 | 5008.68 | 0.041662 | 5150.91 | 0.050078 | 7464.61 | 0.038 | 5233.99 | 0.063092 | 4043.75 | 0.11989 | 5836.74 | 0.098553 | 11270.3 | 0.055511 | 5265.48 | 0.2579 | 6707.14 | 0.24071 | 12719.9 | 0.12001
1009.21 | 0.040715 | 1110.9 | 0.04031 | 1227.74 | 0.039709 | 1226.51 | 0.040512 | 1220.39 | 0.041997 | 1074.84 | 0.045814 | 1137.89 | 0.049283 | 1425 | 0.047304 | 1579.6 | 0.046321 | 1978.17 | 0.044594 | 2351.78 | 0.04358 | 3037.92 | 0.042674 | 3327.34 | 0.046413 | 4166.9 | 0.044415 | 4702.87 | 0.044415 | 4783.5 | 0.054794 | 7058.08 | 0.040108 | 4735.91 | 0.072428 | 3473.54 | 0.15441 | 5176.73 | 0.11822 | 10561 | 0.059895 | 4660.73 | 0.33049 | 5924.95 | 0.30235 | 12039.2 | 0.13027
775.828 | 0.043798 | 854 | 0.043798 | 944.76 | 0.043406 | 943.816 | 0.044907 | 939.108 | 0.047398 | 826.278 | 0.05291 | 1110.9 | 0.049978 | 1344.7 | 0.049185 | 1535.99 | 0.047115 | 1896.81 | 0.045906 | 2266.35 | 0.044817 | 2924.64 | 0.044106 | 3065.38 | 0.050078 | 3889.08 | 0.047398 | 4384.93 | 0.047923 | 4336.96 | 0.062215 | 6754.26 | 0.041997 | 4187.79 | 0.086625 | 3056.2 | 0.19279 | 4341.3 | 0.1569 | 9837.21 | 0.06547 | 4158.58 | 0.42394 | 5120.09 | 0.39528 | 11147 | 0.1494
597.008 | 0.047304 | 657.162 | 0.047827 | 726.277 | 0.047971 | 726.277 | 0.05038 | 721.932 | 0.05463 | 813.976 | 0.053388 | 1075.91 | 0.05109 | 1266.39 | 0.051397 | 1477.24 | 0.048259 | 1813.34 | 0.047541 | 2181.85 | 0.046228 | 2710.61 | 0.047021 | 2795.95 | 0.055014 | 3586.49 | 0.051397 | 4035.67 | 0.052699 | 3936.03 | 0.07071 | 6412.01 | 0.044415 | 3796.85 | 0.10075 | 2633.13 | 0.25534 | 3808.26 | 0.19473 | 9108.18 | 0.072283 | 3673.6 | 0.56998 | 4509.44 | 0.50806 | 10487.3 | 0.16677
459.405 | 0.050988 | 505.188 | 0.052699 | 558.878 | 0.053817 | 558.319 | 0.057893 | 711.895 | 0.055124 | 787.553 | 0.054521 | 1042.03 | 0.052226 | 1158.55 | 0.054904 | 1405.19 | 0.050078 | 1714.59 | 0.04958 | 2081.67 | 0.047923 | 2524.83 | 0.050078 | 2601.72 | 0.05918 | 3337.34 | 0.055511 | 3695.71 | 0.058591 | 3582.9 | 0.080688 | 6099.29 | 0.047021 | 3438.97 | 0.11787 | 2330.71 | 0.32819 | 3354.06 | 0.24435 | 8450.05 | 0.080205 | 3304.13 | 0.74218 | 4121.32 | 0.61868 | 9926.15 | 0.18394
353.164 | 0.055124 | 388.748 | 0.058885 | 430.063 | 0.061534 | 545.079 | 0.058591 | 685.351 | 0.056182 | 755.917 | 0.055957 | 998.177 | 0.053709 | 1078.07 | 0.058183 | 1316.76 | 0.052593 | 1598.67 | 0.052383 | 1958.49 | 0.05038 | 2337.71 | 0.053817 | 2442.87 | 0.063726 | 3016.73 | 0.062401 | 3184.11 | 0.071207 | 3216.11 | 0.094594 | 5761.36 | 0.050279 | 3168.23 | 0.13491 | 2079.59 | 0.4214 | 2962.91 | 0.306 | 7902.45 | 0.088198 | 2998.68 | 0.97515 | 3819.7 | 0.74144 | 9135.54 | 0.21521
271.763 | 0.059715 | 299.146 | 0.066993 | 420.284 | 0.062339 | 526.858 | 0.059895 | 665.096 | 0.057374 | 719.769 | 0.057893 | 944.76 | 0.055901 | 987.257 | 0.062526 | 1232.66 | 0.055401 | 1427.85 | 0.057661 | 1853.68 | 0.052699 | 2106.81 | 0.059596 | 2291.42 | 0.068483 | 2759.84 | 0.069379 | 2832.54 | 0.083981 | 2904.24 | 0.11067 | 5491.34 | 0.053228 | 2910.06 | 0.15518 | 1837.07 | 0.5677 | 2560.42 | 0.39845 | 7294.88 | 0.099344 | 2729.65 | 1.2915 | 3526.03 | 0.90469 | 8374.34 | 0.25508
208.916 | 0.064948 | 294.398 | 0.067599 | 403.401 | 0.063853 | 508.737 | 0.061105 | 641.578 | 0.058709 | 674.473 | 0.060497 | 895.096 | 0.058183 | 912.265 | 0.06706 | 1145.88 | 0.058885 | 1303.65 | 0.06284 | 1733.55 | 0.055957 | 1927.4 | 0.065601 | 2136.51 | 0.074559 | 2469.89 | 0.079726 | 2547.65 | 0.098061 | 2545.11 | 0.13667 | 5228.75 | 0.05635 | 2667.58 | 0.18047 | 1652.31 | 0.73922 | 2255.05 | 0.51163 | 6842.63 | 0.10924 | 2547.65 | 1.6191 | 3350.71 | 1.0427 | 7691.94 | 0.3057
160.763 | 0.071207 | 284.556 | 0.068895 | 381.431 | 0.065864 | 491.239 | 0.062526 | 612.734 | 0.060497 | 616.422 | 0.064689 | 842.127 | 0.060922 | 845.502 | 0.072139 | 1058.84 | 0.063092 | 1198.62 | 0.06821 | 1645.71 | 0.058885 | 1730.09 | 0.074261 | 1964.37 | 0.082896 | 2273.16 | 0.089263 | 2314.45 | 0.11382 | 2261.83 | 0.16693 | 4958.85 | 0.060497 | 2392.1 | 0.2178 | 1499.56 | 0.97223 | 2060.96 | 0.62241 | 6360.92 | 0.12293 | 2340.05 | 2.2341 | 3158.74 | 1.2188 | 7121.89 | 0.36162
123.709 | 0.078696 | 275.044 | 0.070217 | 360.298 | 0.068278 | 452.565 | 0.065864 | 580.524 | 0.06284 | 573.026 | 0.068483 | 784.409 | 0.064624 | 779.717 | 0.078147 | 988.245 | 0.067262 | 1110.9 | 0.073965 | 1532.92 | 0.063092 | 1559.2 | 0.084318 | 1795.3 | 0.093092 | 2046.59 | 0.10329 | 2138.65 | 0.12936 | 2046.59 | 0.19747 | 4707.58 | 0.064624 | 2194.98 | 0.25457 | 1365.02 | 1.289 | 1910.13 | 0.74516 | 6020.52 | 0.13343 | 2188.4 | 2.9738 | 2962.91 | 1.4606 | 6405.6 | 0.45787
95.1004 | 0.088287 | 263.204 | 0.071994 | 336.276 | 0.071421 | 418.188 | 0.069727 | 549.457 | 0.065274 | 535.891 | 0.072428 | 728.459 | 0.068895 | 708.345 | 0.086799 | 904.996 | 0.073449 | 1019.36 | 0.081336 | 1461.07 | 0.06626 | 1427.85 | 0.094405 | 1670.58 | 0.10288 | 1879.81 | 0.11682 | 1990.08 | 0.14512 | 1859.25 | 0.2336 | 4469.04 | 0.069379 | 2000.05 | 0.30205 | 1274.01 | 1.6174 | 1763.27 | 0.90923 | 5574.33 | 0.15257 | 2052.73 | 4.0465 | 2746.08 | 1.8365 | 5942.76 | 0.54435
92.9381 | 0.089263 | 247.629 | 0.074708 | 299.146 | 0.077679 | 386.036 | 0.073965 | 507.213 | 0.06931 | 492.715 | 0.077913 | 674.473 | 0.073817 | 655.849 | 0.094499 | 830.419 | 0.080366 | 932.557 | 0.09016 | 1391.21 | 0.069867 | 1308.88 | 0.10655 | 1565.45 | 0.1128 | 1719.74 | 0.1337 | 1864.83 | 0.16232 | 1685.69 | 0.27744 | 4251.08 | 0.074336 | 1833.4 | 0.35802 | 1170.2 | 2.2319 | 1675.6 | 1.0469 | 5244.46 | 0.16997 | 1976.19 | 5.1082 | 2570.69 | 2.2815 | 5607.88 | 0.62866
89.0265 | 0.091158 | 235.316 | 0.077138 | 268.522 | 0.084402 | 351.402 | 0.079566 | 471.506 | 0.073522 | 447.167 | 0.08525 | 634.559 | 0.078382 | 606.031 | 0.10381 | 753.652 | 0.089442 | 856.566 | 0.10024 | 1322.03 | 0.074039 | 1196.23 | 0.12086 | 1425 | 0.12949 | 1578.02 | 0.15318 | 1721.46 | 0.18579 | 1471.34 | 0.35624 | 4011.53 | 0.080769 | 1733.55 | 0.39845 | 1094.36 | 2.9738 | 1579.6 | 1.2224 | 4963.81 | 0.18709 | 1893.02 | 6.9091 | 2428.25 | 2.8034 | 5286.59 | 0.72676
83.9259 | 0.094028 | 219.408 | 0.080769 | 237.444 | 0.093559 | 317.962 | 0.086625 | 440.069 | 0.077913 | 398.988 | 0.095736 | 595.816 | 0.083312 | 540.736 | 0.11977 | 686.723 | 0.10004 | 778.938 | 0.11336 | 1240.07 | 0.079566 | 1093.27 | 0.13832 | 1315.44 | 0.14614 | 1425 | 0.18084 | 1608.29 | 0.20968 | 1326.01 | 0.4325 | 3793.06 | 0.087671 | 1632.6 | 0.45106 | 1026.52 | 4.0465 | 1481.67 | 1.465 | 4568.45 | 0.21846 | 1840.75 | 9.3919 | 2340.05 | 3.2734 | 5053.96 | 0.82188
79.4346 | 0.096794 | 205.189 | 0.084655 | 212.285 | 0.10371 | 289.146 | 0.094594 | 398.589 | 0.084995 | 353.871 | 0.10881 | 551.66 | 0.09007 | 494.195 | 0.13531 | 641.578 | 0.10881 | 712.608 | 0.12756 | 1180.78 | 0.084318 | 952.348 | 0.17065 | 1211.88 | 0.16544 | 1301.05 | 0.21052 | 1481.67 | 0.2424 | 1176.06 | 0.54544 | 3590.07 | 0.095449 | 1557.64 | 0.498 | 988.245 | 5.1031 | 1373.24 | 1.8401 | 4187.79 | 0.25842 | 1786.35 | 12.4889 | 2237.08 | 4.1655 | 4802.67 | 0.9435
74.2126 | 0.10034 | 190.363 | 0.089353 | 187.341 | 0.1174 | 263.995 | 0.1035 | 365.743 | 0.092535 | 315.428 | 0.12466 | 497.17 | 0.10125 | 453.925 | 0.1518 | 600.001 | 0.11846 | 642.22 | 0.1482 | 1117.59 | 0.09016 | 867.774 | 0.19846 | 1097.65 | 0.19356 | 1198.62 | 0.24313 | 1392.6 | 0.27032 | 1066.27 | 0.66687 | 3394.56 | 0.10392 | 1484.64 | 0.55313 | 946.651 | 6.9022 | 1285.53 | 2.2861 | 3846.54 | 0.30908 | 1738.76 | 17.865 | 2145.07 | 5.4567 | 4513.95 | 1.1307
68.7127 | 0.10486 | 176.431 | 0.094878 | 170.193 | 0.13027 | 240.791 | 0.11393 | 330.607 | 0.10257 | 283.137 | 0.14268 | 460.324 | 0.11078 | 421.126 | 0.16946 | 547.811 | 0.1341 | 583.434 | 0.17099 | 1049.35 | 0.098061 | 791.501 | 0.23127 | 977.434 | 0.235 | 1128.82 | 0.27005 | 1298.45 | 0.30662 | 975.481 | 0.81045 | 3193.68 | 0.1145 | 1419.31 | 0.61437 | 920.513 | 9.3825 | 1214.3 | 2.8062 | 3561.47 | 0.36525 | 1685.69 | 26.3599 | 2069.22 | 7.2344 | 4276.66 | 1.3456
64.1314 | 0.10946 | 160.763 | 0.10247 | 151.856 | 0.14865 | 219.847 | 0.12616 | 296.169 | 0.116 | 251.371 | 0.16693 | 416.935 | 0.12554 | 390.697 | 0.18935 | 512.823 | 0.14688 | 533.752 | 0.19609 | 991.214 | 0.10549 | 729.188 | 0.26576 | 886.19 | 0.27799 | 1065.21 | 0.30084 | 1224.06 | 0.34124 | 888.852 | 0.99984 | 3022.77 | 0.12529 | 1352.79 | 0.68581 | 893.307 | 12.4889 | 1170.2 | 3.2767 | 3203.27 | 0.46109 | 1630.97 | 38.8166 | 1998.05 | 9.8932 | 4015.54 | 1.6567
59.26 | 0.11508 | 147.515 | 0.11056 | 139.342 | 0.16511 | 201.528 | 0.13971 | 268.253 | 0.1304 | 230.426 | 0.18878 | 384.495 | 0.13943 | 354.579 | 0.21933 | 473.395 | 0.16511 | 485.38 | 0.22783 | 902.285 | 0.11977 | 680.57 | 0.29875 | 795.468 | 0.33448 | 1005.18 | 0.33549 | 1141.3 | 0.39017 | 818.056 | 1.2212 | 2843.89 | 0.13846 | 1295.86 | 0.76249 | 869.511 | 17.865 | 1118.7 | 4.1697 | 2971.82 | 0.54763 | 1579.6 | 55.2489 | 1921.63 | 14.1377 | 3823.53 | 2.048
53.6206 | 0.12317 | 130.442 | 0.12478 | 123.462 | 0.19395 | 186.034 | 0.15441 | 245.656 | 0.14556 | 211.438 | 0.21477 | 352.811 | 0.15674 | 333.596 | 0.2424 | 436.999 | 0.18616 | 442.275 | 0.26523 | 840.444 | 0.1321 | 641.578 | 0.33215 | 727.731 | 0.39017 | 952.348 | 0.373 | 1053.56 | 0.45422 | 757.43 | 1.4856 | 2689.01 | 0.1515 | 1230.19 | 0.86402 | 842.97 | 26.3599 | 1072.69 | 5.4622 | 2804.35 | 0.63181 | 1526.8 | 82.0927 | 1870.44 | 18.299 | 3688.33 | 2.4617
48.8588 | 0.13197 | 115.923 | 0.14112 | 108.628 | 0.2315 | 171.903 | 0.17065 | 226.089 | 0.162 | 195.572 | 0.24168 | 324.061 | 0.1769 | 310.732 | 0.27113 | 404.613 | 0.20968 | 389.916 | 0.32885 | 788.341 | 0.14512 | 597.008 | 0.37713 | 686.037 | 0.43467 | 880.888 | 0.43294 | 984.3 | 0.52196 | 701.297 | 1.8146 | 2509.72 | 0.17031 | 1171.37 | 0.98102 | 815.606 | 38.8166 | 1034.76 | 7.2344 | 2643.68 | 0.7304 | 1468.4 | 126.45 | 1815.16 | 26.4656 | 3554.35 | 3.0613
45.2378 | 0.14013 | 103.33 | 0.16071 | 97.8987 | 0.27005 | 156.794 | 0.19375 | 207.044 | 0.18284 | 173.284 | 0.29166 | 297.356 | 0.20086 | 286.269 | 0.30939 | 374.627 | 0.23689 | 362.829 | 0.37375 | 725.551 | 0.16461 | 561.679 | 0.41846 | 649.973 | 0.47513 | 832.082 | 0.48376 | 915.922 | 0.60583 | 640.296 | 2.3675 | 2356.49 | 0.19011 | 1116.47 | 1.1094 | 789.919 | 55.1937 | 999.176 | 9.9031 | 2527.35 | 0.82517 | 1412.23 | 192.068 | 1781 | 35.4048 | 3442.41 | 3.7956
41.5931 | 0.15074 | 92.6597 | 0.1832 | 88.1406 | 0.31754 | 145.755 | 0.21499 | 188.657 | 0.20968 | 153.382 | 0.35802 | 273.672 | 0.22737 | 261.892 | 0.35946 | 351.051 | 0.26391 | 337.286 | 0.42394 | 667.094 | 0.18746 | 531.09 | 0.46201 | 616.422 | 0.5251 | 784.409 | 0.54599 | 872.123 | 0.67021 | 592.844 | 3.0369 | 2201.57 | 0.2137 | 1070.55 | 1.2459 | 763.514 | 82.1748 | 960.958 | 14.1235 | 2401.69 | 0.94823 | 1370.49 | 281.702 | 1749.22 | 49.0994 | 3354.06 | 4.6313
37.635 | 0.16494 | 83.6745 | 0.20885 | 78.9594 | 0.37826 | 134.684 | 0.24143 | 168.162 | 0.24879 | 140.321 | 0.41513 | 245.901 | 0.26924 | 241.515 | 0.41347 | 323.737 | 0.30114 | 320.516 | 0.46619 | 577.629 | 0.23618 | 509.246 | 0.50049 | 587.532 | 0.5757 | 740.208 | 0.61437 | 832.082 | 0.73996 | 548.908 | 4.2582 | 2065.09 | 0.23903 | 1025.49 | 1.4132 | 734.31 | 126.576 | 935.359 | 18.299 | 2257.31 | 1.133 | 1333.99 | 386.392 | 1719.74 | 66.1449 | 3277.8 | 5.748
34.7067 | 0.1785 | 72.2357 | 0.25585 | 70.1008 | 0.46063 | 123.956 | 0.27303 | 150.194 | 0.29726 | 127.222 | 0.49403 | 217.877 | 0.32655 | 212.498 | 0.51522 | 303.06 | 0.33751 | 305.494 | 0.50857 | 504.179 | 0.29726 | 489.768 | 0.54001 | 551.66 | 0.64975 | 701.998 | 0.68581 | 793.879 | 0.82106 | 516.426 | 5.9765 | 1948.72 | 0.26549 | 981.352 | 1.6272 | 706.223 | 192.068 | 907.715 | 26.4656 | 2138.65 | 1.3496 | 1301.05 | 505.654 | 1687.37 | 90.1838 | 3216.11 | 6.8199
31.8149 | 0.19492 | 61.9876 | 0.32105 | 62.9874 | 0.55147 | 115.576 | 0.30417 | 138.786 | 0.3365 | 119.933 | 0.5449 | 197.933 | 0.38475 | 192.276 | 0.61621 | 274.22 | 0.40125 | 294.103 | 0.54708 | 457.113 | 0.35199 | 470.564 | 0.58149 | 521.094 | 0.72749 | 669.768 | 0.75718 | 765.042 | 0.89211 | 492.223 | 8.2387 | 1846.28 | 0.29195 | 941.93 | 1.8623 | 685.351 | 281.702 | 890.632 | 35.4048 | 2008.07 | 1.6617 | 1282.96 | 599.954 | 1660.59 | 119.683 | 3130.44 | 8.6007
28.8449 | 0.21693 | 55.2536 | 0.3836 | 55.5306 | 0.68787 | 106.797 | 0.34398 | 130.182 | 0.37375 | 112.948 | 0.601 | 175.727 | 0.47229 | 175.551 | 0.72458 | 253.644 | 0.46109 | 278.086 | 0.60704 | 409.498 | 0.42863 | 440.509 | 0.6609 | 490.258 | 0.82435 | 626.364 | 0.87445 | 735.044 | 0.97906 | 476.244 | 10.9118 | 1759.75 | 0.32009 | 905.902 | 2.1573 | 667.094 | 386.392 | 874.744 | 49.0994 | 1912.04 | 2.05 | 1282.96 | 599.954 | 1632.6 | 162.69 | 3068.45 | 10.5049
26.8948 | 0.23594 | 50.2462 | 0.44702 | 50.1458 | 0.82517 | 98.7838 | 0.39056 | 123.215 | 0.40773 | 106.69 | 0.66554 | 157.108 | 0.57801 | 161.569 | 0.841 | 231.119 | 0.54381 | 267.182 | 0.65628 | 381.813 | 0.48765 | 417.77 | 0.73701 | 461.246 | 0.93598 | 597.606 | 0.97029 | 706.93 | 1.0788 | 464.486 | 13.9411 | 1677.28 | 0.35234 | 874.744 | 2.4939 | 650.623 | 505.654 | 859.999 | 66.0788 | 1844.43 | 2.4666 | 1282.96 | 599.954 | 1608.29 | 212.906 | 3001.68 | 12.8693
24.6046 | 0.26338 | 46.2904 | 0.5106 | 45.2378 | 0.98989 | 90.6435 | 0.45106 | 116.971 | 0.44568 | 98.3895 | 0.76939 | 143.299 | 0.68034 | 150.796 | 0.95584 | 211.438 | 0.63689 | 257.735 | 0.70528 | 361.38 | 0.53678 | 389.526 | 0.85201 | 439.19 | 1.0375 | 561.679 | 1.1195 | 677.853 | 1.1946 | 454.833 | 17.9366 | 1585.93 | 0.3937 | 848.891 | 2.8543 | 641.578 | 599.954 | 843.813 | 90.1838 | 1777.44 | 3.0674 | 1282.96 | 599.954 | 1590.7 | 261.086 | 2930.5 | 15.8607
22.6222 | 0.29459 | 43.2905 | 0.57283 | 42.0111 | 1.1386 | 83.5073 | 0.5178 | 111.044 | 0.48814 | 92.7524 | 0.86057 | 129.144 | 0.826 | 140.883 | 1.0962 | 188.657 | 0.7865 | 246.887 | 0.76708 | 343.756 | 0.58851 | 367.576 | 0.96256 | 424.084 | 1.1228 | 530.559 | 1.2787 | 657.162 | 1.2902 | 443.604 | 24.6024 | 1486.13 | 0.44971 | 818.056 | 3.4036 | 641.578 | 599.954 | 830.419 | 119.683 | 1721.46 | 3.7994 | 1282.96 | 599.954 | 1567.01 | 337.259 | 2872.47 | 19.1604
20.4081 | 0.3392 | 40.8511 | 0.63118 | 39.4855 | 1.2787 | 78.5656 | 0.57686 | 104.682 | 0.53893 | 85.9644 | 0.99088 | 120.173 | 0.94633 | 131.358 | 1.2534 | 173.457 | 0.92945 | 234.611 | 0.84861 | 330.277 | 0.63625 | 347.558 | 1.0842 | 407.863 | 1.2322 | 504.179 | 1.4446 | 633.292 | 1.4245 | 434.385 | 32.7154 | 1408 | 0.503 | 791.501 | 4.0022 | 641.578 | 599.954 | 816.422 | 162.69 | 1677.28 | 4.636 | 1282.96 | 599.954 | 1543.68 | 431.321 | 2798.75 | 24.382
18.8203 | 0.38283 | 38.5492 | 0.69687 | 37.3351 | 1.4288 | 74.8087 | 0.63181 | 99.5772 | 0.58851 | 82.0176 | 1.0875 | 112.835 | 1.0702 | 123.092 | 1.4288 | 163.847 | 1.0406 | 221.391 | 0.95872 | 314.169 | 0.70176 | 327.318 | 1.2335 | 395.018 | 1.3176 | 485.865 | 1.5775 | 615.19 | 1.5278 | 428.775 | 44.4714 | 1342.01 | 0.55869 | 764.277 | 4.9226 | 641.578 | 599.954 | 804.267 | 212.906 | 1639.14 | 5.7537 | 1282.96 | 599.954 | 1528.32 | 513.81 | 2746.08 | 29.1322
17.6712 | 0.42309 | 35.8712 | 0.79044 | 35.979 | 1.5386 | 69.7511 | 0.71451 | 93.7783 | 0.65563 | 77.5508 | 1.2139 | 106.264 | 1.1994 | 116.855 | 1.5934 | 153.843 | 1.1851 | 208.29 | 1.0929 | 297.952 | 0.77634 | 310.111 | 1.3935 | 382.195 | 1.4217 | 472.45 | 1.697 | 595.22 | 1.6801 | 421.969 | 63.045 | 1260.08 | 0.64136 | 739.468 | 6.0185 | 641.578 | 599.954 | 795.468 | 261.086 | 1608.29 | 6.8199 | 1282.96 | 599.954 | 1519.18 | 558.834 | 2680.95 | 36.0839
16.6421 | 0.46712 | 33.4795 | 0.89301 | 34.4991 | 1.675 | 65.8207 | 0.796 | 86.309 | 0.76173 | 73.3274 | 1.3578 | 101.588 | 1.3163 | 109.939 | 1.8255 | 145.319 | 1.3376 | 198.528 | 1.2115 | 283.988 | 0.85371 | 296.466 | 1.5416 | 367.209 | 1.5681 | 456.2 | 1.8679 | 572.453 | 1.8792 | 417.77 | 81.8468 | 1213.09 | 0.70036 | 715.464 | 7.4324 | 641.578 | 599.954 | 783.625 | 337.259 | 1565.45 | 8.6007 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2625.24 | 44.1612
15.6729 | 0.5204 | 31.6562 | 0.9889 | 33.246 | 1.8091 | 62.423 | 0.87445 | 79.9126 | 0.8762 | 70.2411 | 1.4886 | 96.5377 | 1.4635 | 104.682 | 2.0296 | 136.993 | 1.5248 | 190.363 | 1.3269 | 268.79 | 0.95393 | 282.289 | 1.7451 | 354.579 | 1.7157 | 439.629 | 2.0582 | 554.425 | 2.0562 | 414.441 | 110.481 | 1162.03 | 0.7779 | 695.709 | 9.2336 | 641.578 | 599.954 | 771.959 | 431.752 | 1534.45 | 10.5049 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2552.75 | 57.7919
14.8045 | 0.57859 | 29.664 | 1.1116 | 31.9744 | 1.9736 | 58.7878 | 0.98397 | 74.5846 | 0.99884 | 66.7486 | 1.6617 | 92.9381 | 1.5822 | 98.9816 | 2.3137 | 130.703 | 1.6953 | 183.081 | 1.4591 | 256.706 | 1.0479 | 270.678 | 1.9345 | 342.041 | 1.8754 | 421.126 | 2.316 | 539.116 | 2.2408 | 411.55 | 141.295 | 1106.47 | 0.87883 | 681.251 | 11.2104 | 641.578 | 599.954 | 764.277 | 513.81 | 1501.06 | 12.8821 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2494.71 | 71.5824
14.2098 | 0.62803 | 27.2467 | 1.2967 | 30.8746 | 2.1273 | 56.1448 | 1.081 | 69.8908 | 1.133 | 63.3664 | 1.8661 | 89.1155 | 1.7382 | 93.3106 | 2.6534 | 124.453 | 1.8981 | 176.255 | 1.5918 | 244.675 | 1.157 | 263.204 | 2.0831 | 330.607 | 2.0459 | 407.048 | 2.5494 | 526.331 | 2.425 | 409.088 | 177.301 | 1064.14 | 0.97029 | 664.431 | 14.1235 | 641.578 | 599.954 | 759.706 | 558.834 | 1465.46 | 15.8765 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2435.55 | 90.0036
13.5033 | 0.70036 | 25.4047 | 1.4797 | 29.7234 | 2.3114 | 53.7817 | 1.1792 | 65.5579 | 1.2851 | 60.4571 | 2.0727 | 85.5357 | 1.9019 | 89.8313 | 2.912 | 118.739 | 2.1358 | 170.875 | 1.7243 | 232.742 | 1.289 | 254.66 | 2.2792 | 318.28 | 2.2701 | 393.835 | 2.809 | 515.394 | 2.6035 | 405.018 | 231.563 | 1022.42 | 1.0799 | 642.863 | 19.6062 | 641.578 | 599.954 | 757.43 | 599.954 | 1436.45 | 19.1412 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2373.04 | 116.03
12.7934 | 0.78965 | 23.9013 | 1.6567 | 28.7873 | 2.4939 | 51.6729 | 1.2787 | 62.1738 | 1.4302 | 57.7391 | 2.3206 | 81.2827 | 2.1401 | 85.1091 | 3.3329 | 113.061 | 2.4202 | 165.163 | 1.8754 | 223.616 | 1.4203 | 246.887 | 2.5014 | 304.884 | 2.557 | 379.909 | 3.12 | 504.683 | 2.843 | 402.595 | 300.621 | 984.3 | 1.2006 | 625.112 | 26.4391 | 641.578 | 599.954 | 757.43 | 599.954 | 1399.58 | 24.4064 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2321.41 | 142.43
11.9763 | 0.9202 | 22.6902 | 1.8273 | 27.6862 | 2.7206 | 49.6965 | 1.3866 | 58.8466 | 1.6029 | 55.1984 | 2.5957 | 77.4733 | 2.4033 | 80.7158 | 3.8491 | 108.086 | 2.7097 | 160.442 | 2.0094 | 212.71 | 1.5918 | 239.83 | 2.7206 | 295.873 | 2.809 | 368.681 | 3.4275 | 494.69 | 3.1014 | 400.187 | 377.606 | 950.445 | 1.3309 | 610.899 | 34.6344 | 641.578 | 599.954 | 757.43 | 599.954 | 1373.24 | 29.1614 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2259.57 | 179.801
11.4036 | 1.0448 | 21.6268 | 2.0094 | 26.5475 | 3.0127 | 47.6048 | 1.5172 | 55.8089 | 1.7911 | 52.7695 | 2.912 | 73.8425 | 2.6908 | 76.3199 | 4.5034 | 103.641 | 3.0491 | 155.233 | 2.203 | 204.574 | 1.7469 | 231.581 | 3.0067 | 284.272 | 3.1672 | 359.578 | 3.7428 | 484.894 | 3.3664 | 398.589 | 478.594 | 912.265 | 1.5066 | 595.816 | 47.316 | 641.578 | 599.954 | 757.43 | 599.954 | 1340.67 | 36.0839 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2208.19 | 226.977
10.9128 | 1.1804 | 20.7788 | 2.1811 | 25.532 | 3.2997 | 45.1023 | 1.6902 | 53.1402 | 1.9894 | 50.8527 | 3.2344 | 71.018 | 2.9738 | 73.6213 | 5.0271 | 99.7766 | 3.4036 | 150.345 | 2.3985 | 196.749 | 1.9248 | 224.512 | 3.3063 | 277.531 | 3.4689 | 349.999 | 4.1323 | 473.869 | 3.7093 | 397.793 | 577.006 | 875.619 | 1.7209 | 583.434 | 63.1712 | 641.578 | 599.954 | 757.43 | 599.954 | 1312.81 | 44.1612 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2157.98 | 279.458
10.4744 | 1.3349 | 19.8844 | 2.3937 | 24.6292 | 3.6141 | 43.2905 | 1.8568 | 50.4475 | 2.223 | 48.6637 | 3.6761 | 68.3016 | 3.2964 | 71.018 | 5.6285 | 96.1523 | 3.807 | 144.739 | 2.6614 | 189.792 | 2.1145 | 216.357 | 3.6724 | 268.522 | 3.8878 | 343.412 | 4.4631 | 464.486 | 4.079 | 397.793 | 599.954 | 837.927 | 1.9914 | 571.881 | 88.1332 | 641.578 | 599.954 | 757.43 | 599.954 | 1276.56 | 57.7919 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2113.14 | 339.628
10.1141 | 1.4901 | 19.1429 | 2.6035 | 23.8536 | 3.9347 | 41.2204 | 2.0603 | 47.9392 | 2.4964 | 46.99 | 4.1158 | 65.1657 | 3.7541 | 68.5069 | 6.3525 | 93.2173 | 4.2412 | 139.621 | 2.9708 | 181.623 | 2.3794 | 209.543 | 4.083 | 263.995 | 4.2412 | 336.276 | 4.8883 | 456.656 | 4.4364 | 397.793 | 599.954 | 813.976 | 2.2319 | 561.679 | 120.163 | 641.578 | 599.954 | 757.43 | 599.954 | 1247.54 | 71.654 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2065.09 | 424.899
9.8054 | 1.6551 | 18.3739 | 2.8601 | 23.1717 | 4.2412 | 39.3279 | 2.2884 | 45.3284 | 2.843 | 45.3738 | 4.6221 | 62.9244 | 4.1323 | 66.3493 | 7.1481 | 90.5529 | 4.7296 | 134.28 | 3.3429 | 173.457 | 2.7043 | 204.984 | 4.432 | 257.735 | 4.6966 | 329.287 | 5.3594 | 449.858 | 4.7867 | 397.793 | 599.954 | 787.553 | 2.5316 | 553.871 | 161.071 | 641.578 | 599.954 | 757.43 | 599.954 | 1217.95 | 90.0036 | 1282.96 | 599.954 | 1514.63 | 599.954 | 2020.15 | 519.493
9.4021 | 1.9114 | 17.742 | 3.1107 | 22.0858 | 4.8542 | 37.7858 | 2.5039 | 43.5511 | 3.1577 | 43.7694 | 5.2218 | 60.9427 | 4.5487 | 64.5173 | 8.0112 | 88.1406 | 5.3007 | 128.757 | 3.8146 | 166.157 | 3.0491 | 199.923 | 4.859 | 252.884 | 5.1595 | 322.122 | 5.9467 | 442.275 | 5.2166 | 397.793 | 599.954 | 765.042 | 2.8543 | 546.717 | 227.659 | 641.578 | 599.954 | 757.43 | 599.954 | 1186.69 | 116.03 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1986.1 | 596.962
9.1334 | 2.1273 | 17.166 | 3.3664 | 21.3902 | 5.3433 | 35.9071 | 2.8147 | 41.8016 | 3.4933 | 42.1373 | 5.9467 | 58.7878 | 5.0878 | 62.8615 | 8.9607 | 85.4502 | 6.0487 | 125.202 | 4.2369 | 160.121 | 3.4241 | 195.572 | 5.3007 | 248.373 | 5.748 | 316.692 | 6.5068 | 435.69 | 5.6794 | 397.793 | 599.954 | 744.662 | 3.2312 | 540.736 | 310.397 | 641.578 | 599.954 | 757.43 | 599.954 | 1160.87 | 142.43 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.8901 | 2.3889 | 16.5425 | 3.6908 | 20.7788 | 5.8407 | 34.6374 | 3.0613 | 40.1224 | 3.8839 | 40.7695 | 6.7318 | 57.2217 | 5.5892 | 60.9427 | 10.2969 | 83.3404 | 6.8609 | 122.355 | 4.6267 | 154.768 | 3.8184 | 191.126 | 5.8994 | 243.211 | 6.4938 | 311.043 | 7.1624 | 429.203 | 6.2454 | 397.793 | 599.954 | 725.551 | 3.665 | 536.427 | 403.773 | 641.578 | 599.954 | 757.43 | 599.954 | 1129.95 | 179.801 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.7141 | 2.6454 | 15.9098 | 4.079 | 20.2455 | 6.3334 | 33.513 | 3.3096 | 38.5106 | 4.3225 | 39.525 | 7.6129 | 55.6418 | 6.1833 | 59.557 | 11.7381 | 80.7965 | 8.1894 | 119.693 | 5.1544 | 150.495 | 4.1655 | 187.341 | 6.4808 | 237.206 | 7.4472 | 304.884 | 7.9157 | 420.705 | 7.0065 | 397.793 | 599.954 | 704.107 | 4.2795 | 533.752 | 503.132 | 641.578 | 599.954 | 757.43 | 599.954 | 1104.26 | 226.977 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.5074 | 3.0097 | 15.3319 | 4.508 | 19.7062 | 6.9438 | 32.5551 | 3.5496 | 37.0376 | 4.8251 | 38.5106 | 8.5322 | 54.1595 | 6.7859 | 58.6703 | 13.2215 | 78.6442 | 9.7167 | 117.206 | 5.7825 | 147.515 | 4.49 | 183.448 | 7.2271 | 232.742 | 8.4136 | 297.952 | 9.1052 | 411.55 | 7.9553 | 397.793 | 599.954 | 686.037 | 4.9424 | 532.153 | 556.047 | 641.578 | 599.954 | 757.43 | 599.954 | 1079.15 | 279.458 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.3223 | 3.407 | 14.9085 | 4.8834 | 19.2774 | 7.5221 | 31.4668 | 3.8607 | 35.9071 | 5.2585 | 37.5222 | 9.6008 | 52.8223 | 7.4846 | 57.5661 | 15.3152 | 76.5492 | 11.7499 | 114.312 | 6.5919 | 144.739 | 4.8348 | 179.995 | 8.0273 | 228.362 | 9.5434 | 292.344 | 10.2148 | 403.805 | 9.0056 | 397.793 | 599.954 | 668.43 | 5.771 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1056.72 | 339.628 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.1331 | 3.9703 | 14.4535 | 5.3754 | 18.8203 | 8.2552 | 30.3845 | 4.2412 | 35.0556 | 5.6173 | 36.6691 | 10.6636 | 51.6213 | 8.247 | 56.5392 | 18.1531 | 74.6592 | 14.237 | 112.61 | 7.3584 | 142.299 | 5.2323 | 176.431 | 8.9966 | 224.064 | 11.0545 | 286.842 | 11.6097 | 398.589 | 9.9428 | 397.793 | 599.954 | 649.973 | 6.9368 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1032.69 | 424.899 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
8.012 | 4.472 | 14.0403 | 5.9171 | 18.3923 | 9.0507 | 29.3982 | 4.6452 | 34.19 | 6.0548 | 36.051 | 11.8561 | 50.7004 | 9.0417 | 55.6418 | 22.128 | 72.9616 | 17.7937 | 110.049 | 8.5835 | 139.9 | 5.6908 | 173.978 | 10.0126 | 219.847 | 12.7923 | 281.443 | 13.4213 | 393.835 | 11.0545 | 397.793 | 599.954 | 636.466 | 7.9553 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 1010.22 | 519.493 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.869 | 5.1287 | 13.6526 | 6.5787 | 18.0823 | 9.8635 | 28.4439 | 5.1184 | 33.4126 | 6.5459 | 35.5143 | 13.103 | 49.8458 | 9.9726 | 54.978 | 26.5717 | 72.0193 | 20.0223 | 107.978 | 9.8932 | 137.542 | 6.2392 | 170.704 | 11.2328 | 215.494 | 15.1931 | 276.699 | 15.3458 | 387.583 | 12.5264 | 397.793 | 599.954 | 621.994 | 9.4578 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 993.199 | 596.962 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.7596 | 5.8935 | 13.4091 | 7.084 | 17.7597 | 10.7493 | 27.274 | 5.7537 | 32.751 | 7.0136 | 35.0205 | 15.057 | 49.202 | 10.8791 | 54.5945 | 32.2606 | 71.374 | 22.575 | 105.84 | 11.4598 | 135.088 | 6.9646 | 167.994 | 12.5892 | 210.804 | 18.2077 | 272.307 | 17.4065 | 381.813 | 14.2797 | 397.793 | 599.954 | 609.678 | 11.1656 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.6441 | 6.7588 | 13.078 | 7.8448 | 17.4953 | 11.6913 | 26.5475 | 6.2454 | 31.9744 | 7.6281 | 34.4991 | 17.9725 | 48.276 | 12.377 | 54.5945 | 39.839 | 70.4522 | 26.5451 | 103.952 | 13.4482 | 132.546 | 7.7822 | 165.825 | 14.025 | 206.424 | 22.8247 | 267.985 | 20.0623 | 376.505 | 16.0361 | 397.793 | 599.954 | 596.412 | 13.3543 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.5378 | 7.6587 | 12.7296 | 8.7394 | 17.2866 | 12.8436 | 25.8144 | 6.7995 | 31.404 | 8.2058 | 34.1559 | 20.4472 | 47.32 | 14.3513 | 54.5945 | 49.0994 | 69.8209 | 30.5036 | 101.996 | 16.2948 | 130.573 | 8.6525 | 163.519 | 15.5156 | 202.741 | 28.5554 | 262.416 | 24.2361 | 371.642 | 18.2441 | 397.793 | 599.954 | 584.018 | 16.3601 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.4479 | 8.8008 | 12.4526 | 9.7361 | 17.0634 | 14.2512 | 25.1771 | 7.3584 | 30.7821 | 8.8626 | 33.816 | 24.4064 | 46.6155 | 16.5907 | 54.5945 | 65.095 | 69.1954 | 35.3694 | 99.4777 | 21.2604 | 128.5 | 9.707 | 161.407 | 17.4937 | 199.125 | 34.8777 | 258.768 | 27.7669 | 366.842 | 20.9858 | 397.793 | 599.954 | 574.748 | 18.9697 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.3738 | 10.266 | 12.1939 | 10.9555 | 16.8767 | 15.7658 | 24.7032 | 7.9157 | 30.2028 | 9.7361 | 33.6137 | 28.6412 | 45.8756 | 19.7242 | 54.5945 | 85.5285 | 68.5069 | 43.5038 | 98.0947 | 25.5553 | 126.587 | 10.8791 | 159.482 | 19.7242 | 195.768 | 45.9635 | 255.17 | 32.1318 | 360.298 | 24.5042 | 397.793 | 599.954 | 565.625 | 22.6882 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.3078 | 12.303 | 11.9644 | 12.6903 | 16.6921 | 17.6343 | 24.2383 | 8.4981 | 29.7531 | 10.4316 | 33.5466 | 33.7792 | 45.4646 | 23.3792 | 54.5945 | 123.575 | 67.8931 | 54.2633 | 97.0216 | 30.0495 | 124.952 | 12.0956 | 157.58 | 22.3952 | 192.661 | 59.2549 | 251.623 | 37.1085 | 354.934 | 28.2148 | 397.793 | 599.954 | 555.535 | 27.2171 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.2423 | 14.7588 | 11.8335 | 14.011 | 16.5425 | 19.823 | 23.8536 | 9.2059 | 29.2809 | 11.4827 | 33.4795 | 39.2852 | 45.0122 | 27.4906 | 54.5945 | 170.008 | 67.3521 | 67.7516 | 95.7685 | 36.8128 | 123.215 | 13.997 | 155.856 | 25.9935 | 189.792 | 75.6297 | 248.125 | 42.8561 | 350.349 | 33.2431 | 397.793 | 599.954 | 547.811 | 31.8439 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1918 | 17.599 | 11.6923 | 15.6715 | 16.3943 | 22.3058 | 23.4749 | 10.0326 | 28.9895 | 12.3399 | 33.3125 | 47.1742 | 44.6089 | 32.8794 | 54.5945 | 228.115 | 66.8823 | 88.398 | 95.0054 | 43.0709 | 121.38 | 16.0522 | 154.151 | 29.249 | 187.341 | 94.9974 | 245.165 | 48.4653 | 345.133 | 39.1675 | 397.793 | 599.954 | 538.039 | 38.1622 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1416 | 21.3456 | 11.5992 | 17.5639 | 16.2637 | 25.3517 | 23.0792 | 10.9884 | 28.7298 | 13.3543 | 33.1796 | 57.1025 | 44.3864 | 39.0502 | 54.5945 | 306.081 | 66.3493 | 117.196 | 93.8721 | 52.8178 | 119.933 | 18.781 | 152.312 | 34.3584 | 184.737 | 124.318 | 242.24 | 56.3086 | 340.335 | 46.892 | 397.793 | 599.954 | 530.559 | 45.78 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1416 | 24.9243 | 11.5182 | 19.8627 | 16.1502 | 28.7272 | 22.804 | 11.8798 | 28.3587 | 15.254 | 33.0802 | 69.1895 | 44.1651 | 49.3949 | 54.54 | 429.599 | 66.1506 | 161.233 | 93.0311 | 67.2118 | 118.384 | 21.9737 | 150.495 | 40.8067 | 182.716 | 159.309 | 239.112 | 64.5118 | 336.612 | 57.3314 | 397.793 | 599.954 | 522.66 | 53.8848 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.1202 | 30.3515 | 11.4608 | 22.1723 | 16.0536 | 32.1318 | 22.5319 | 13.0116 | 28.302 | 17.4937 | 32.9811 | 84.6774 | 44.0768 | 60.2106 | 54.54 | 520.533 | 65.8865 | 210.366 | 92.0134 | 85.9572 | 117.206 | 25.4024 | 148.551 | 53.5624 | 181.26 | 207.027 | 236.023 | 76.696 | 333.596 | 67.4812 | 397.793 | 599.954 | 514.879 | 64.7056 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.106 | 36.9974 | 11.3809 | 25.6065 | 15.9416 | 37.2945 | 22.2854 | 14.1235 | 28.302 | 20.264 | 32.9152 | 98.1846 | 44.0768 | 76.696 | 54.54 | 577.584 | 65.8865 | 270.657 | 91.3715 | 104.988 | 116.155 | 29.6317 | 147.368 | 64.1259 | 179.995 | 258.747 | 233.441 | 88.8411 | 330.277 | 83.3334 | 397.793 | 599.954 | 506.2 | 85.443 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0989 | 50.1414 | 11.3581 | 30.0195 | 15.8939 | 42.9848 | 22.13 | 15.5156 | 28.302 | 24.1877 | 32.9152 | 120.043 | 44.0328 | 103.839 | 54.54 | 599.954 | 65.8865 | 332.57 | 90.8249 | 126.703 | 114.885 | 35.868 | 146.193 | 76.4662 | 178.74 | 325.985 | 230.888 | 101.58 | 327.645 | 104.151 | 397.793 | 599.954 | 498.663 | 110.261 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0705 | 63.9338 | 11.3468 | 34.669 | 15.8621 | 49.4938 | 21.9976 | 17.0618 | 28.302 | 28.8135 | 32.9152 | 146.914 | 43.9888 | 130.823 | 54.54 | 599.954 | 65.8865 | 414.823 | 90.3719 | 155.066 | 113.969 | 42.8132 | 144.884 | 98.0865 | 177.493 | 415.238 | 228.133 | 122.223 | 326.011 | 127.721 | 397.793 | 599.954 | 492.223 | 139.191 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0635 | 116.146 | 11.3468 | 118.729 | 15.8621 | 57.6188 | 21.8879 | 18.7622 | 28.302 | 35.0525 | 32.9152 | 184.352 | 43.8132 | 176.593 | 54.54 | 599.954 | 65.8865 | 491.692 | 89.8313 | 201.714 | 113.061 | 51.9794 | 144.017 | 115.451 | 176.431 | 499.123 | 225.864 | 146.914 | 323.737 | 167.645 | 397.793 | 599.954 | 485.38 | 185.091 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 316.667 | 11.3468 | 149.134 | 15.8463 | 69.1203 | 21.8879 | 21.0488 | 28.302 | 45.5061 | 32.9152 | 229.488 | 43.7694 | 238.853 | 54.54 | 599.954 | 65.8865 | 566.147 | 89.3833 | 255.66 | 112.497 | 61.2429 | 142.869 | 141.012 | 175.903 | 559.393 | 223.616 | 178.19 | 323.09 | 205.377 | 397.793 | 599.954 | 480.55 | 232.258 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 484.856 | 11.3354 | 599.954 | 15.8463 | 504.139 | 21.8879 | 23.7088 | 28.302 | 58.9593 | 32.9152 | 271.741 | 43.6819 | 305.47 | 54.54 | 599.954 | 65.8865 | 599.954 | 88.7598 | 336.249 | 111.601 | 74.9521 | 142.299 | 170.861 | 175.2 | 599.954 | 221.391 | 209.108 | 322.767 | 271.741 | 397.793 | 599.954 | 475.768 | 300.922 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 543.404 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 27.8225 | 28.302 | 74.6529 | 32.9152 | 367.18 | 43.6382 | 375.347 | 54.54 | 599.954 | 65.8865 | 599.954 | 88.3171 | 422.78 | 111.267 | 87.0819 | 141.873 | 216.34 | 175.2 | 599.954 | 220.067 | 251.602 | 322.445 | 341.672 | 397.793 | 599.954 | 471.506 | 379.499 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 32.4547 | 28.302 | 86.8211 | 32.9152 | 453.435 | 43.464 | 473.832 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.8766 | 513.81 | 110.712 | 106.043 | 141.731 | 278.621 | 175.2 | 599.954 | 218.75 | 299.122 | 322.122 | 418.573 | 397.793 | 599.954 | 468.217 | 486.313 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 38.623 | 28.302 | 108.185 | 32.9152 | 529.458 | 43.3772 | 550.514 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.701 | 578.74 | 110.27 | 127.593 | 141.306 | 359.549 | 175.2 | 599.954 | 217.659 | 362.075 | 322.122 | 528.928 | 397.793 | 599.954 | 465.881 | 570.124 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 45.8258 | 28.302 | 129.781 | 32.9152 | 573.555 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.939 | 173.964 | 141.306 | 461.21 | 175.2 | 599.954 | 216.357 | 446.684 | 321.479 | 577.584 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 56.7609 | 28.302 | 164.654 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.61 | 223.598 | 141.306 | 569.554 | 175.2 | 599.954 | 215.494 | 553.827 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 68.4326 | 28.302 | 205.789 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 109.391 | 282.549 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 80.2261 | 28.302 | 248.353 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.954 | 347.878 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 94.4291 | 28.302 | 301.826 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.519 | 424.899 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 113.96 | 28.302 | 377.606 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 108.194 | 488.262 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 135.077 | 28.302 | 467.244 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.87 | 568.984 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 155.999 | 28.302 | 552.721 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 186.391 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 223.151 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 282.266 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 346.836 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 424.05 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 500.623 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 565.015 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954
7.0564 | 599.954 | 11.3354 | 599.954 | 15.8304 | 599.954 | 21.8879 | 565.015 | 28.302 | 599.954 | 32.9152 | 599.954 | 43.2905 | 599.954 | 54.54 | 599.954 | 65.8865 | 599.954 | 87.5258 | 599.954 | 107.762 | 599.954 | 141.165 | 599.954 | 175.2 | 599.954 | 214.633 | 599.954 | 321.479 | 599.954 | 397.793 | 599.954 | 464.022 | 599.954 | 531.621 | 599.954 | 641.578 | 599.954 | 757.43 | 599.954 | 991.214 | 599.954 | 1282.96 | 599.954 | 1514.63 | 599.954 | 1982.13 | 599.954